# Temperature Mapping Version 10 - Help

# About Temperature Mapping and this Tool

## Background

No matter the country, the average cold-room at a country’s central level may hold millions of dollars’ worth of vaccines.  In highly populated countries this may apply as well to provincial and in some cases to district level cold-rooms. The WHO Effective Vaccine Management (EVM) sets standards for safe vaccine handling and storage to ensure that heat and freezing temperatures do not damage vaccines.  It requires all vaccine cold and freezer-rooms to be temperature mapped routinely every two years. The first temperature mapping should take place at the time of the storage unit’s commissioning. Temperature mapping should also be performed when the cold- and freezer-rooms, as well as associated storage units (refrigerators and freezers) undergo any modifications or major repairs. See Annex 1: When to conduct temperature mapping after modifications or major repairs.

Temperature mapping is not limited to cold and freezer rooms. Refrigerators and freezers can also be temperature mapped using this application. It is required for dry stores as well, where diluents, injection equipment and other pharmaceuticals are kept.

## The problem

The high cost of vaccines justifies temperature mapping of all vaccine cold and freezer rooms and vaccine storage units on a routine basis.  That being said, EVM assessments completed to date by national immunization programmes have not documented thoroughly and effectively temperature distribution within cold-rooms.  There are several reasons for this situation:

- The lack of trained immunization program managers and store managers and the lack of a simple tool to facilitate carrying out a temperature mapping exercise;

- the dependence on expatriates as external consultants to carry out these studies; and

- the technical requirements and standards for temperature mapping.  For example, temperature mapping requires at least 48 hours of continuous temperature recording with an appropriate number of temperature sensors (pre-qualified by WHO) placed accurately within empty and fully stocked storage units. This can entail costs not necessarily budgeted for.

## The solution

One practical solution is to empower and equip field-level Expanded Programme on Immunization (EPI) program staff, and especially store managers, to conduct temperature mapping.  This can be achieved through a number of simple, well-defined, clearly explained and step-by-step actions assisted by an affordable computer-based application accessible and available to the national EPI staff.

## The importance of temperature mapping

Temperature mapping is the process of recording and mapping temperatures within a three-dimensional space, such as cold- and freezer-rooms, dry storage areas, refrigerators and freezers. Temperatures will not be the same everywhere within the storage area.  Even in a small refrigerator or in a well-designed cold or freezer room, and particularly in a large warehouse, temperatures can vary by as much as 10° C from one location to another within the same space.  Temperatures in the corners will most likely be different from those measured in the centre and close to cooling units.  In dry stores, the temperatures close to the ceiling tend to be higher than those close to the floor. There are as well specific areas within the cold-rooms where the temperature will differ, for example next to the cooling fans where the temperature will be at its coldest, or close to the doors where it is likely to be at its warmest.

Temperature mapping and temperature monitoring are integral to the storage of pharmaceuticals’ efficacy and for appropriate storage conditions.  Good manufacturing practice for pharmaceutical products recommends regular temperature mappings of all kind of warehouses.

## The temperature mapping process

Temperature mapping consists of several key steps:

- Deciding when to perform temperature mapping;

- Placing an appropriate number of sensors in different areas, particularly areas that might go above or below specified safe temperature ranges.  Generally, 20 sensors are used to temperature map a medium-sized cold storage unit, with an additional sensor to measure the ambient temperature.  Temperatures are recorded at a specified regular interval, continuously, for a period of at least 48 hours;

- Reading and transferring recoded temperatures (minimum, maximum, mean and mean kinetic) to a three-dimensional sketch of the storage vessel (cold- and freezer-rooms, dry storage areas and equipment, such as refrigerators and freezers) to be temperature mapped;

- Identifying areas where vaccines and thermo-sensitive pharmaceutical products should not be stored; and,

- Taking action to reduce the exposure of vaccines and pharmaceuticals to incorrect temperatures.

## A simplified process

The temperature mapping tool consists of a multi-lingual guide (English, French, Spanish, Russian and Arabic at the time of publication of this guide) and computer application in MS Excel®.  It automatically develops a simple three-dimensional sketch of a storage area, be it a cold-room, freezer room, refrigerator/freezer or a dry store.  It requires specifying the unit’s length, width and height, as well as:

- the number, location and the dimensions of the door(s)

- the number, location and dimensions of the evaporators

- the number, location and dimensions of the shelves, and

- the number and location of the sensors.

This information is entered into the application. The application includes a specially designed measurement form for recording the temperature data.  This form simplifies taking measurements and transferring them to the application.

The process allows for the placement of an appropriate number of sensors in pre-specified locations within the three-dimensional sketch and thereafter placing the sensors in the correct spot within the storage area or unit to be mapped.  The application allows placing up to 12 required sensors in pre-specified positions, beginning with three sensors in each of the four corners of the unit to be temperature mapped.  There is also the option of positioning an additional 28 sensors in places that might be considered risky areas for storing specific items, such as vaccines.

After completing the temperature recording over a period of at least 48 hours (the Application allows up to 72 hours), the application imports temperature records (converted to Excel format).  It ascribes the temperature readings to the location of the sensors, and colour codes the areas where temperatures fall outside the desired range using the three-dimensional drawing.

The application produces a report based on the summarized temperature recording data. It includes a summary of key findings.  A standard format is provided to facilitate the preparation of reports. The user needs to use his/her judgment to decide whether or not the storage room or equipment tested is adequate for storing specific items (vaccines and other pharmaceutical products) and to identify safe and risky areas within the unit.

The computer application takes care of the most complicated part, this being the drawing of the sketch of the unit with an appropriate scale to fit an A4 sheet for printing.  The most critical part of the mapping will be taking accurate 3-dimensional measurements of a minimum of eight places in the unit.

## How to use this Guide

This guide provides a step-by-step approach to temperature map the storage area or equipment.  The temperature mapping application presented in this guide is applicable to cold and freezer rooms, refrigerators and freezers and dry stores.  Once you have read the guide and completed the initial exercise, you have learned how to perform temperature mapping.  Systematic follow-up of the steps provided in this guide is essential for successful temperature mapping.

## Equipment and material required for temperature mapping

### Hardware requirements

The following items are required for temperature mapping, using this application:

- A minimum of 21 temperature monitoring sensors (temperature data loggers)

- A computer with Windows® and MS Excel® installed

- A tape-measure

- A clipboard for recording information on the measurement form

- Warm clothes for working in the cold and freezer rooms.

Six brands of temperature monitoring devices (sensors), tested and approved by WHO, are used by this version of the temperature mapping application:

### Temperature monitoring devices tested for this tool

Six brands of temperature monitoring devices tested and approved by WHO are compatible with this version of the temperature mapping application:

| Devices | Model | PQS Number |
| --- | --- | --- |
| LogTag® | TRIX-8 | E06/006 |
| Q-Tag® | CLm doc LR | E06/016 |
| Libero® | Ti1-L | E06/024 |
| Honeywell® | BluTag360 | E06/079 |
| LogTag ® | ULTRID-16 | E006/012 |
| NT ® | Pbro | E006/074 |

For more detail information refer to the official site of each of the above devices presented in settings sheet.  For more detailed information refer to Sensors and Settings sheets.

| LogTag® (TRIX-8) with interface | Q-tag® (CLm doc LR) | Libero® (Ti1-L) |
| --- | --- | --- |

| Honeywell BluTag360® | LogTag UTRID-16® | NT bpro® |
| --- | --- | --- |

It should be noted that the use of temperature monitoring devices (sensors) is NOT limited to six types tested by this tool and listed in Settings and Test sheets.  You can use any other device provided that the results are presented according to the format compatible with this tool. For further information related to compatibility of results, refer to Data and Sensors sheets.

## When to conduct temperature mapping

WHO Effective Vaccine Management recommends temperature mapping of cold rooms and freezer rooms every two years.

Different pharmaceutical companies have different regulations and schedules for temperature mapping.

Temperature mapping for commissioning of new cold and freezer rooms is essential.  Temperature mapping is the only way that the new equipment is well designed, adequately built and correctly installed.  Without a thorough temperature mapping, one cannot ensure the new cold and freezer rooms are suitable for the products intended to be stored in.

This tool also makes estimation of Hold-over Time test available.   Estimation of hold-over time helps users to know the period of time between when the cooling units are turned-off and when “the mean internal temperature” and/or when “the first sensor detects” the critical temperature.

In addition, after any major repair, the cold and freezer rooms should be temperature mapped.  Annex 1 -    When to conduct temperature mapping after modifications or major repairs, provides a detailed list of repairs made on cold and freezer after which a temperature mapping is required.

Temperature mapping is not limited to active cold chain equipment.  Dray store and temperature-controlled areas should also be temperature mapped on specific schedules.

## Enabling macros

If you see this message, it means the macros are not enabled in you PC!

Enable macros before using this tool.

For more information and to enable macros please refer to "EnableMacros" document in Temperature Mapping folder in Common Files!

Enable Macros Help Document

Important: If this is the first time using this tool, a warning message may appear on the

screen.

This means that you should first enable macros in the computer before starting to use the application.  As the method to enable macros differs across operating systems, instructions to enable macros are provided in detail in several languages in the file ‘EnableMacros’.

# Annex 1: When to conduct temperature mapping after modifications or major repairs

This list is not exhaustive and any additional repairs not listed must be discussed between Departmental Manager, QA Manager and Engineers/Technicians to deduce the risk and to decide on whether mapping is required or not.

- Full refurbishment of walk-in fridge / freezer

- Change of Compressor on walk-in fridge freezer, upright fridge, freezer or incubator.

- Re-gassing of Compressor – may be a top-up of gas or full re-gas. Implications must be discussed with engineer and decision taken locally on whether to re-map or not

- Change of Fan Motor or fan motor bearings for evaporator or condenser

- Change driving and non-driving end bearings followed by lubrication with correct grade of motor bearing lubricant

- Circulation fan motor changed

- Door catches, locks and hinge changed (external doors)

- Door seal replaced due to significant irreparable damage or Door seal to be replaced before significant damage

- Pipework and pipe insulation replacement or repair

- Replacement of any badly worn fixed and moving contacts

- Replacement or adjustment of thermostat

- Total freezer defrosts and maintenance (for walk in freezer only). Defrost only may not require remapping but will need to be discussed with engineer to consider risks

- Replacement of system valves

- Shut down of control panel where associated plant items will also be shut down. In many cases there will be separate plant to run the cold rooms but in cases of only one system then this will require remapping

- Check each stage and function of multi stage relay (step controller) in accordance with its associated controller output and ensure correct operation

- For cold stores using DX Air Conditioning Units to maintain temperature:

  - Check condensate pump replace if necessary. Examples of minor repair / maintenance which should not routinely result in a requirement to remapping a facility

  - Replacement of electrical wiring mains lead; mains plug and plug wiring

  - Adjustment of door catches locks and hinge operation

  - System valves checked

  - Fans checked for alignment and adjustment as required

  - Operational test of condenser unit

  - Inspection of drives pulleys and impellers for wear and adjustment as necessary

  - Checking of chassis and drain tray for condensate leaks and drain tube for free flow

  - Cleaning of air-cooled refrigeration condenser filter and condenser

  - Checking of all pipe connections for leaks

  - Check set cut out points for general calibration and wear

  - Check control thermostats for correct temperature sets and operation

  - Removal of build-up of ice on doors and seals

  - Capillary defrost system

  - Forced defrost timer / system check

  - Verification of defrost heater function

  - Checking of freezer center temperature with digital thermometer and record instrument delay

  - Lubrication of driving and non-driving end bearings with correct grade of motor bearing lubricant

  - Carry out insulation test of motor and record motor running current • Check fixed and moving contacts for wear and replace any badly worn contacts

  - Electric motors - check that the commutations of open type machines is satisfactory i.e. slip rings or commutators appear to be satisfactory and brushes do not require renewal. Check slip rings or commutator enclosure for carbon or metal deposits and that slip rings are not worn or grooved

  - Check operation of condensate pump

  - Sterilize clean and flush if necessary

  - Ensure cable terminals to be checked

  - Pipework and seals to be checked

  - Check on correct condensate discharge into drain

For more information: Consult Jacob, D (2011). Temperature Mapping in Pharmaceuticals. Pharma Treasures. https://pharmatreasures.blogspot.ca/2011/10/temperature-mapping-in-pharmaceuticals.html. Blog posted 15 October 2011.

# References

Choundhary A (undated). SOP for Temperature Mapping Study. Pharmaceutical guidelines. https://www.pharmaguideline.com/2008/02/sop-for-procedure-for-temperature.html. Undated blog.

Drucker, B (2013). Proper storage and shipping of pharmaceuticals with the aid of temperature mapping. Ezine @articles. http://ezinearticles.com/?Proper-Storage-And-Shipping-Of-Pharmaceuticals-With-The-Aid-Of-Temperature-Mapping&id=7941976. Blog submitted 17 August 2013.

Gibson, AC (2011). Warehouse temperature mapping explained. Ezine @rticles. http://ezinearticles.com/?Warehouse-Temperature-Mapping-Explained&id=6192578. Blog posted 18 April 2011

Jacob, D (2011). Temperature Mapping in Pharmaceuticals. Pharma Treasures. https://pharmatreasures.blogspot.ca/2011/10/temperature-mapping-in-pharmaceuticals.html. Blog posted 15 October 2011

Vaisala (2011). Vailsala Application Note : Eight Steps to Validating/Mapping a Chamber. Vailsala : Helsinki, Finland. http://www.vaisala.com/Vaisala%20Documents/Application%20notes/LSH-8-Steps-to-Mapping-Validation-Project.pdf

Weddle, GB and Benton RL (2004). Temperature Mapping and Monitoring: Quality-Control Tools for Pharmaceutical and Medical Device Warehousing. Johnson Controls, INc : Milwaukee, USA. http://www.johnsoncontrols.com/content/dam/WWW/jci/be/commercial/capabilities/my_building__vertical/life_sciences/articles_and_white/Temp_Mapping_White_Paper.pdf

Green A. Temperature Mapping : How to Perform and Document http://www.tutelamedical.com/wp-content/uploads/2011/11/Temperature_mapping.pdf

Temperature Mapping  http://www.ellab.com/applications/temperature-mapping.aspx

Temperature Mapping  http://www.biomap.co.uk/biomap-services/temperature-mapping.php

The Requirement for Temperature Mapping http://www.validation-online.net/temperature-mapping.html

Last update: 04 September 2024

A 40 m3 cold-room may have approximately US $ 2,500,000 of vaccines when fully loaded.

WHO (2016). WHO/UNICEF Joint Statement. Achieving immunization targets with the comprehensive effective vaccine management (EVM) framework. 10 March 2016. WHO Reference WHO/IVB/16.09. Available at: http://apps.who.int/iris/bitstream/10665/254717/1/WHO-IVB-16.09-eng.pdf?ua=1

Jacob, D (2011). Temperature Mapping in Pharmaceuticals. Pharma Treasures. A blog dated 15 October 2011, available at: https://pharmatreasures.blogspot.ca/2011/10/temperature-mapping-in-pharmaceuticals.html

See Clause 3.19 of Pharmaceutical Inspection Co-operation Scheme (PIC/s) (2017) Guide to Good Manufacturing Practice for Medicinal Products. Available at: https://www.picscheme.org/en/publications?tri=gmp

Mean kinetic temperature (MKT) is a simplified way of expressing the overall effect of temperature fluctuations during storage or transit of perishable goods. The MKT is widely used in the pharmaceutical industry.