## 1. Weight of chlorine powder
How to determine the weight of chlorine powder required to prepare a chlorine liquid solution
1. Input the volume of liquid chlorine solution required in litres (L)
2. Input the desired active chlorine concentration in the final liquid chlorine solution in percentage (%)
3. Input the concentration of active chlorine in the chlorine powder in percentage (%)
Where possible, test the strength of the chlorine powder before use; if not possible to do this, check the estimated concentration with the manufacturer/supplier
In general, if using bleaching powder - use 35 %; if using high test hypochlorite - use 70 %
| Total volume of liquid chlorine solution required | 1 | L
| Desired concentration of final chlorine liquid solution | 1 | %
| Active chlorine concentration in the chlorine powder | 30 | %
| Weight of chlorine powder required | 33.3333 | g
or
|  | 0.033333 | kg

## 2. Chlorine dose rate
How to calculate the chlorine dose rate
1. Input the plant flow rate in litres per hour (L/h)
2. Input the active chlorine concentration in the chlorine liquid solution in percentage (%)
3. Input the required chlorine dose (i.e. Chlorine Demand + Desired Chlorine Residual) in milligrams per litre (mg/L)
The chlorine dose rate will be calculated in millilitres per hour (mL/h)
| Plant Flow Rate | 100000 | L/h
| Active Chlorine Concentration in the Chlorine Liquid Solution | 1 | %
| Required Chlorine Dose | 3 | mg/L
| Chlorine Dose Rate Required | 30000 | mL/h
or
|  | 500 | mL/minute

## 3. Actual chlorine dose
To estimate the actual chlorine dose:
1. Input the plant flow rate in litres per hour (L/h)
2. Input the active chlorine concentration in the chlorine liquid solution in percentage (%)
3. Input the current chlorine dose rate in millilitres per hour (mL/h)
The actual chlorine dose will be calculated in milligrams per litre (Note - this is the theoretical chlorine dose and does not take chlorine demand into consideration).
| Plant Flow Rate | 100000 | L/hr
| Active Chlorine Concentration in the Chlorine Liquid Solution | 1 | %
| Chlorine Dose Rate | 30000 | mL/hr
| Chlorine Concentration | 3 | mg/L