## Slide 1
Principles and Practices of Drinking-water Chlorination
A guide to strengthening chlorination practices in
small- to medium-sized water supplies

## Slide 2: NOTE TO TRAINER(S):
Delete this slide prior to delivering the presentation.
This PowerPoint presentation and the associated training materials have been developed by the World Health Organization (2017) for adaptation and use by those conducting training on this topic.
All reasonable precautions have been taken to verify the information contained in these materials. However, the material is being distributed without warranty of any kind, either expressed or implied. The responsibility for the interpretation and use of the material lies with the reader. In no event shall the World Health Organization be liable for damages arising from its use.
Notes: 2

## Slide 3
Part 1. Chlorination Principles
  What is chlorination?
  Properties of chlorine
  Principles of drinking-water chlorination
    - Chlorine dose
    - Types of chlorine present in drinking-water
    - Chlorine demand
    - Chlorine decay
    - Ct concept for disinfection
    - Aesthetic considerations for chlorination
    - Optimizing the chlorine concentration in a water supply system
    - Points of chlorine application
  Summary
Part 2. Practical Chlorination
  Safe handling and storage of chlorine
  Chlorine liquid dosing systems
  Chlorine dosing calculations
  Developing standard operating procedures
  Chlorine monitoring
General Summary
Contents

## Slide 4
Upon completion of this training course, you will be able to:
understand the key principles of drinking-water chlorination
apply these principles practically in the field
perform the basic calculations required to support effective drinking-water chlorination
develop standard procedures to correctly and consistently chlorinate drinking-water
store and handle chlorine safely
Aim of this training programme

## Slide 5
Part 1. Chlorination Principles
Describes the key chlorination concepts in a practical context to provide the necessary understanding for effective chlorination of drinking-water.

## Slide 6
Part 1. Chlorination Principles
  What is chlorination?
Contents

## Slide 7
Microorganisms – Found in almost all environments
Microorganisms
SOIL
AIR
WATER
DOMESTIC/INDUSTRIAL WASTE
Photo credit: Shutterstock.com

## Slide 8
Microorganisms in drinking-water may cause illness
Microorganisms commonly associated with waterborne disease include:
• bacteria (e.g., Escherichia coli, Vibrio cholerae)
• viruses (e.g., Hepatitis A, poliovirus A)
• protozoa (e.g., Cryptosporidium, Giardia).
BACTERIA
VIRUSES
PROTOZOA
Photo credit: Shutterstock.com

## Slide 9
Chlorination
Addition of chlorine disinfectant to drinking-water to kill or inactivate microorganisms
Chlorine is a powerful disinfectant that kills most harmful microorganisms associated with waterborne disease
Chlorine does not kill all harmful microorganisms
Photo credit: Shutterstock.com

## Slide 10
Relative effectiveness of chlorine
SOIL
AIR
WATERWAYS
SEWAGE
BACTERIA
VIRUSES
PROTOZOA
Most effective Effectiveness of chlorine Least effective
Photo credit: Shutterstock.com

## Slide 11
Part 1. Chlorination Principles
  What is chlorination?
  Properties of chlorine
Contents

## Slide 12
Properties of chlorine
May remain in the water after disinfection has occurred
Very reactive
Corrosive
Characteristic odour
Volatile once exposed to air
(i.e. escapes from water into the air)

## Slide 13
Properties of chlorine
Chlorine may be found in three forms
Powder
Liquid
Gas
Photo credit: Shutterstock.com

## Slide 14
Chlorine gas typically contains pure chlorine
Chlorine powder and liquid do not contain pure chlorine
  are mixed with other substances (e.g., calcium, sodium or water)
The strength of chlorine in chlorine powder or chlorine liquid is referred to as the ‘concentration’ of chlorine in that substance
Typically, this is expressed as the percentage (%) of active chlorine present
How to express the strength of chlorine

## Slide 15
Properties of chlorine: Powder
Powder
Appearance: White powder, granules or tablet
Strength: Typically 30 to 70 % active chlorine
Requires mixing with water to make a liquid solution before use (see ‘Chlorine liquid’ below)
Stability: May lose strength over time; more stable than chlorine liquid
Application: Typically used for small-sized water treatment plants (< 5 000 cubic meters per day)
Examples: => Bleaching powder (approx. 35 % active chlorine)
=> High test hypochlorite (approx. 70 % active chlorine)
Photo credit: Shutterstock.com

## Slide 16
Properties of chlorine: Liquid
Liquid
Appearance: Pale yellow to clear liquid
Strength: Typically 1 to 15 % active chlorine
Stability: May lose strength over time; less stable than chlorine powder
Application: Typically used for small- to medium-sized water treatment plants (i.e., <10 000 cubic meters per day)
Examples: => Sodium hypochlorite (10 to 15 % active chlorine)
=> Domestic bleach (5 to 10 % active chlorine)
=> Chlorine liquid solution prepared from chlorine powder (typically 1 to 5 % active chlorine)
Photo credit: Shutterstock.com

## Slide 17
Properties of chlorine: Gas
Gas
Appearance: Green-yellow gas
Strength: Approx. 100 % active chlorine
Stability: Most stable
Application: Typically used for medium- to large-sized water treatment plants (i.e., >10, 000 cubic meters per day)
Example: Chlorine gas (liquefied)
Photo credit: Shutterstock.com

## Slide 18
Part 1. Chlorination Principles
  What is chlorination?
  Properties of chlorine
  Principles of drinking-water chlorination
    - Chlorine dose
Contents

## Slide 19
Chlorine dose
How much chlorine is added to the drinking-water (or, the concentration of chlorine in the drinking-water)
Usually expressed as milligrams per litre (mg/L).
  for example, if drinking-water has a chlorine concentration of 1 mg/L, this means that there is 1 milligram of chlorine present in 1 litre of water

## Slide 20
Part 1. Chlorination Principles
  What is chlorination?
  Properties of chlorine
  Principles of drinking-water chlorination
    - Chlorine dose
    - Types of chlorine present in drinking-water
Contents

## Slide 21
Chlorine reactions in drinking-water
WATERWAYS
SEWAGE
Chlorine Dose
Amount of chlorine added to the water
Residual Chlorine
Free chlorine available for disinfection (may prevent recontamination of water)
Combined chlorine
Chlorine bound to organic and nitrogen compounds (weak disinfection capacity)
Chlorine Demand
Chlorine consumed during reaction with organic and inorganic material present
Total Chlorine
Chlorine remaining after chlorine demand has been satisfied and disinfection has occurred

## Slide 22
Residual chlorine (or free chlorine, or free available chlorine)
Chlorine remaining after disinfection has taken place
An effective disinfectant
Presence of residual chlorine indicates that:
    disinfection has occurred
    the disinfected water has a degree of residual protection from microbial recontamination (e.g., during storage and distribution)
  WHO recommends that a minimum residual chlorine concentration of 0.2 mg/L is maintained to the point of delivery to the consumer1.
1 World Health Organization (2011). Guidelines for Drinking-water Quality. 4th Edn. Geneva, Switzerland.

## Slide 23
Chlorine demand
When chlorine is added to water, it reacts with any organic and inorganic material (chlorine reactive substances)
  during these reactions, chlorine is consumed
    referred to as the ‘chlorine demand’
  as chorine is consumed during these reactions, the concentration of chlorine decreases

## Slide 24
Chlorine demand
It is important to understand how much chlorine will be consumed during the disinfection process:
  This allows you to estimate how much chlorine you need to add to the drinking-water at the water treatment plant to ensure there will be sufficient residual chlorine present in the water to protect the water during storage and distribution

## Slide 25
Chlorine demand
Understanding the chlorine demand of the raw water is important for effective disinfection
  if the water has a higher concentration of chlorine reactive substances, the chlorine demand will be higher
  if the water has a lower concertation of chlorine reactive substances, the chlorine demand will be lower

## Slide 26
Relationship between chlorine demand & chlorine dose
WATERWAYS
DIRTY WATER
High concentration of organic & inorganic material
High chlorine demand
(i.e. high chlorine consumption)
CLEAN WATER
Low concentration of organic & inorganic material
Low chlorine demand
(i.e. low chlorine consumption)
Photo credit: Shutterstock.com

## Slide 27
Chlorine demand
Chlorine demand of water is constantly changing
  Changes as water quality changes
Examples of events that influence the chlorine demand include….

## Slide 28
Seasonal changes in the raw water quality (e.g. dry/wet season, algal blooms, floods, landslides, bushfires)

## Slide 29
Failure of a water treatment process (e.g. sedimentation, filtration)

## Slide 30
Introduction of contamination post treatment (e.g. leaking/bust water main, accumulation of sediment or microbial biofilm within water mains)

## Slide 31
Chlorine demand
Consideration of the chlorine demand is most important at the water treatment plant, immediately prior to the addition of chlorine
Where practical, chlorine demand is a useful parameter to monitor
Where routine monitoring is not practical, you should be aware of the impact of changing raw water quality (i.e. changing chlorine demand) on the required chlorine dose
E.g. poorer water quality => higher chlorine demand => higher chlorine dose required

## Slide 32
Part 1. Chlorination Principles
  What is chlorination?
  Properties of chlorine
  Principles of drinking-water chlorination
    - Chlorine dose
    - Types of chlorine present in drinking-water
    - Chlorine demand
    - Chlorine decay
Contents

## Slide 33
Chlorine decay
=> The decrease (or reduction) in the concentration of chlorine in drinking-water as it passes from the water treatment plant, through the distribution system, to the point of consumer delivery
Due to chlorine decay, the concentration of chlorine at the end of the distribution system will usually be less then the concentration at the water treatment plant

## Slide 34
Chlorine decay
The rate and extent of chlorine decay may be influenced by:
  the level of chlorine reactive substances that are present in the treated water as well as the distribution tanks and pipes (i.e., organic and inorganic material)
  the type of material used in the distribution network tanks, pipes and fittings
  how long the water remains in the distribution system (or the ‘water age’)

## Slide 35
Chlorine decay
WATERWAYS
Water Treatment Plant
FILTRATION
CHLORINATION
CHLORINE CONCENTRATION:
1.0 mg/L
Intermediate Storage Tank
CHLORINE CONCENTRATION:
0.7 mg/L
CHLORINE CONCENTRATION:
0.0 mg/L
CHLORINE CONCENTRATION:
0.0 mg/L
CHLORINE CONCENTRATION:
0.5 mg/L
CHLORINE CONCENTRATION:
0.2 mg/L
SOURCE WATER
DISTRIBUTION SYSTEM
BRANCH A
BRANCH B
BRANCH C
BRANCH D
Low usage area
Unclean pipes/
Biofilm
Sediment accumulation

## Slide 36
Understanding the chlorine demand and chlorine decay of your water supply system is important:
    helps you to determine the correct chlorine dose at the water treatment plant
Remember, must dose enough chlorine at the water treatment plant to ensure you have ≥ 0.2 mg/L at the point of consumer delivery.

## Slide 37
Strategies to minimize chlorine decay in a water supply system
Optimize water treatment process to ensure high quality treated water (i.e., water entering the distribution system has a low chlorine demand)
Maintain intermediate storages and distribution pipes (e.g., for removal of accumulated sediment and microbial biofilms)
Optimize the hydraulic regime during distribution (i.e., minimise water age and low-flow/stagnant areas)
Minimize unaccounted water (i.e., leaks, illegal connections) which may be vulnerable points for entry of contamination
Aim for 24 hours supply (where feasible) to maintain positive pressure in the system to minimize risks of contamination entry

## Slide 38
Part 1. Chlorination Principles
  What is chlorination?
  Properties of chlorine
  Principles of drinking-water chlorination
    - Chlorine dose
    - Types of chlorine present in drinking-water
    - Chlorine demand
    - Chlorine decay
    - Ct concept for disinfection
Contents

## Slide 39
Ct concept for disinfection
Chlorine requires time to kill or inactive microorganisms during disinfection
this is referred to as ‘contact time’
The contact time must be considered in conjunction with the chlorine concentration and other factors, to ensure that effective disinfection of drinking-water occurs
    this is referred to as the ‘Ct’ concept for disinfection
  The Ct value is the product of disinfectant concentration and contact time with the drinking-water
  Ct = Residual Chlorine Concentration (mg/L) x Time of Contact (min)

## Slide 40
Factors influencing the Ct value
1. Chlorine concentration
3. pH of water
2. Temperature of water
Ct value

## Slide 41
Influence of chlorine concentration on disinfection
High
(>3 mg/L)
Low
(<0.4 mg/L)
LESS
contact time needed
MORE contact time needed
RESIDUAL CHLORINE

## Slide 42
Influence of water temperature on disinfection
Cooler
(<5 oC)
LESS
contact time or lower chlorine concentration needed
MORE
contact time or higher chlorine concentration needed
WATER TEMPERATURE
Warmer
(>20 oC)

## Slide 43
Influence of pH on disinfection
pH measures if the water is acid or alkaline (or basic)
  measured on a scale of pH 0 to pH 14
  pH 7 considered neutral, pH <7 considered acidic and pH >7 considered alkali
LESS
contact time or lower chlorine concentration needed
MORE
contact time or higher chlorine concentration needed
pH Scale
ACIDIC
NEUTRAL
ALKALI
Optimum pH for drinking-water

## Slide 44
Influence of pH on disinfection
For effective chlorination, the pH of the water should be < pH 8.0
However
To balance water quality considerations, including chlorination, the optimum pH of drinking-water is generally between pH 6.5 and pH 8.5
  Where water is >pH 8.0, higher chlorine concentrations or more contact time will be required!

## Slide 45
Turbidity may also indirectly impact contact time
Suspended organic/inorganic particles in water
  gives water an opaque (or cloudy) appearance
Turbidity may influence the effectiveness of chlorine disinfection
  indicates the presence of chlorine reactive substances, which may react with and consume chlorine, thereby increasing the chorine demand
  May also ‘shields’ microorganisms from the lethal/inactivating effects of chlorine
1000 NTU
1 NTU
LESS
contact time or lower chlorine concentration needed
MORE
contact time or higher chlorine concentration needed
TURBIDITY
High
Low
Photo credit: Shutterstock.com

## Slide 46
Type of microorganism and chlorine disinfection
SOIL
AIR
WATERWAYS
SEWAGE
BACTERIA
VIRUSES
PROTOZOA
Most effective Least effective
LESS
contact time or lower chlorine concentration needed
MORE
contact time or higher chlorine concentration needed
Photo credit: Shutterstock.com

## Slide 47
Minimum required contact time for effective disinfection
How much contact time is needed for effective disinfection?
  For effective disinfection, the WHO1 recommends at least 30 minutes contact time, where the residual chlorine concentration is ≥0.5 mg/L and the pH of the water is <pH 8.
1 World Health Organization (2011). Guidelines for Drinking-water Quality. 4th Edn. Geneva, Switzerland.
Minimum recommendation only – should determined on a site-specific basis (more to follow on this in Part 2…)

## Slide 48
Part 1. Chlorination Principles
  What is chlorination?
  Properties of chlorine
  Principles of drinking-water chlorination
    - Chlorine dose
    - Types of chlorine present in drinking-water
    - Chlorine demand
    - Chlorine decay
    - Ct concept for disinfection
    - Aesthetic considerations for chlorination
Contents

## Slide 49
Chlorine may result in a distinctive taste & odour in drinking-water
  different individuals vary in their ability to detect chlorine taste/odour
  in general, chlorine has a taste/odour threshold >0.3 mg/L
If chlorine is present in drinking-water at concentrations that are unacceptable to consumers:
  may result in an individual using alternative, less safe, water sources
Aesthetic considerations (i.e. relating to taste or odour)
Photo credit: Shutterstock.com

## Slide 50
For this reason the aesthetic impact of chlorine on drinking-water should be considered when optimizing the chlorine dose
HOWEVER…
Disinfection should always be prioritized over aesthetic considerations!!!
Aesthetic considerations (i.e. relating to taste, odour, appearance)

## Slide 51
Aesthetic considerations
To balance effective disinfection against aesthetic considerations:
  a residual chlorine concentration of between 0.2 to 0.5 mg/L should be targeted at all points in the distribution network
However, this may need to be higher in certain circumstances, to ensure a minimum residual chlorine concentration of 0.2 mg/L is maintained to the point of consumer delivery
  discussed further in next section…

## Slide 52
Part 1. Chlorination Principles
  What is chlorination?
  Properties of chlorine
  Principles of drinking-water chlorination
    - Chlorine dose
    - Types of chlorine present in drinking-water
    - Chlorine demand
    - Chlorine decay
    - Ct concept for disinfection
    - Aesthetic considerations for chlorination
    - Optimizing the chlorine concentration in a water supply system
Contents

## Slide 53
Optimizing the chlorine dose
Requires balancing the following key considerations…
OPTIMUM CHLORINE DOSE
Adequate Disinfection at the Water Treatment Plant
Adequate Residual Disinfection Capacity during Storage & Distribution
Customer Acceptability

## Slide 54
Optimizing the chlorine dose
Aesthetically unacceptable
Too high
(e.g. >1.5 mg/L)
Too low
(<0.2 mg/L)
RESIDUAL CHLORINE CONCENTRATION
Risk of microbial contamination
Photo credit: Shutterstock.com

## Slide 55
Optimizing the chlorine dose
Priority must always be to add sufficient chlorine such that:
  The minimum required contact time for effective disinfection is achieved
  The residual chlorine concentration at all points in distribution system is ≥0.2 mg/L
To balance effective disinfection against consumer acceptability considerations:
  a residual chlorine concentration of between 0.2 to 0.5 mg/L in the distribution network should be targeted
Effective disinfection and residual protection should always be prioritized over aesthetic considerations

## Slide 56
Optimizing the chlorine dose
May need to maintain a higher residual chlorine concentration in some parts of the distribution system to ensure a minimum residual chlorine concentration of 0.2 mg/L is achieved throughout the entire system
  for example, having a higher residual chlorine earlier in the system
  this may be needed to maintain an adequate residual chlorine concentration at the very end of the distribution system

## Slide 57
WATERWAYS
Water Treatment Plant
FILTRATION
CHLORINATION
CHLORINE CONCENTRATION:
1.0 mg/L
Intermediate Storage Tank
CHLORINE CONCENTRATION:
0.7 mg/L
CHLORINE CONCENTRATION:
0.0 mg/L
CHLORINE CONCENTRATION:
0.0 mg/L
CHLORINE CONCENTRATION:
0.5 mg/L
CHLORINE CONCENTRATION:
0.2 mg/L
SOURCE WATER
DISTRIBUTION SYSTEM
BRANCH A
BRANCH B
BRANCH C
BRANCH D
Optimizing the chlorine dose
CHLORINE CONCENTRATION:
1.2 mg/L
CHLORINE CONCENTRATION:
0.9 mg/L
CHLORINE CONCENTRATION:
0.2 mg/L
CHLORINE CONCENTRATION:
0.2 mg/L
CHLORINE CONCENTRATION:
0.7 mg/L
CHLORINE CONCENTRATION:
0.4 mg/L
Current chlorine dose at the water treatment plant is too low to maintain >0.2 mg/L at all points in the distribution system
Increased chlorine dose at the water treatment plant ensures >0.2 mg/L is maintained at all points in the distribution system

## Slide 58
Part 1. Chlorination Principles
  What is chlorination?
  Properties of chlorine
  Principles of drinking-water chlorination
    - Chlorine dose
    - Types of chlorine present in drinking-water
    - Chlorine demand
    - Chlorine decay
    - Ct concept for disinfection
    - Aesthetic considerations for chlorination
    - Optimizing the chlorine concentration in a water supply system
    - Points of chlorine application
Contents

## Slide 59
Points of chlorine dosing
Chlorine may be added:
Pre-chlorination (before water treatment plant)
Primary chlorination (after water treatment process)
Secondary chlorination (during distribution)
Water Treatment Plant
Distribution Network
2. Primary chlorination
3. Secondary chlorination
1. Pre-chlorination

## Slide 60
Points of chlorine dosing
Pre-chlorination (before water treatment plant)
  used to remove minerals (e.g. Iron, manganese)
  chlorine makes them insoluble (particulate)
  can be removed during water treatment (filtration)
  can also remove taste/odour
Potential issues:
  raw water may have a high chlorine demand which requires high chlorine dose (high operational cost)
  formation of disinfection by-products in high organic waters
Water Treatment Plant
Distribution Network
Pre-chlorination

## Slide 61
Points of chlorine dosing
61
4/01/2024
2. Primary chlorination (after water treatment)
  used for disinfection; most common & effective point of application
  most effective to add chlorine when turbidity is as low as possible – ideally <1 NTU (i.e., after clarification, filtration)
  clean, filtered water so lower chlorine demand
    use less chlorine
    less risk of disinfection by-product formation
      Disinfection should not be compromised in attempting to control disinfection by-products
Water Treatment Plant
Distribution Network
Primary chlorination

## Slide 62
Points of chlorine dosing
3. Secondary (‘booster’) chlorination
  used to maintain sufficient chlorine concentration during distribution to protect the water from recontamination i.e. ≥0.2 mg/L
  ‘booster station’ adds more chlorine to the water at strategic points during distribution when the chlorine concentration is too low i.e. <0.2 mg/L
  helps keep the water safe to the very end of the distribution system
  common in large distribution networks
Water Treatment Plant
Distribution Network
Secondary chlorination

## Slide 63
Part 1. Chlorination Principles
  What is chlorination?
  Properties of chlorine
  Principles of drinking-water chlorination
    - Chlorine dose
    - Types of chlorine present in drinking-water
    - Chlorine demand
    - Chlorine decay
    - Ct concept for disinfection
    - Aesthetic considerations for chlorination
    - Optimizing the chlorine concentration in a water supply system
    - Points of chlorine application
  Summary
Contents

## Slide 64
Summary of the optimal conditions required for effective chlorination
Turbidity: <1 NTU (lower where possible)
(where < 1 NTU is not possible, <5 NTU should be the aim; above 5 NTU, disinfection should still be practised, but higher chlorine doses or contact times will be required to inactivate harmful microorganisms)
pH: <pH 8.0
(Above pH 8.0, chlorination should still be practised but higher chlorine doses or contact times will be required to inactivate harmful microorganisms)
Minimum contact time: 30 minutes contact time with a minimum residual chlorine concentration of 0.5 mg/L, where the pH of the water is <pH 8.

## Slide 65
A minimum residual chlorine concentration of 0.2 mg/L must always be maintained to the point of consumer delivery
The residual chlorine concentration during distribution to the point of delivery should aim to be between 0.2 to 0.5 mg/L
    may need to be higher than 0.5 mg/L in particular circumstances to ensure that a minimum residual chlorine concentration of 0.2 mg/L is always maintained
The concentration of chlorine in water supplied to consumers should always be <5 mg/L
Summary of the optimal conditions required for effective chlorination

## Slide 66
Part 2. Practical Chlorination
Applies key chlorination principles into practice, describing safe and effective procedures for drinking-water chlorination.

## Slide 67
Part 2. Practical Chlorination
  Safe handling and storage of chlorine
  Chlorine liquid dosing systems
  Chlorine dosing calculations
    How to calculate the chlorine demand
    How to calculate the Ct value
    How to calculate the required chlorine dose
    How to calculate the amount of chlorine powder required to make a chlorine liquid solution
    How to calculate the chlorine dose rate
  Developing standard operating procedures
  Chlorine monitoring
General Summary
Contents

## Slide 68
Part 2. Practical Chlorination
  Safe handling and storage of chlorine
Contents

## Slide 69
Remember…Properties of chlorine
May remain in the water after disinfection has occurred (i.e. residual protection)
Very reactive
Corrosive
Characteristic odour
Volatile once exposed to air

## Slide 70
Safe handling and storage of chlorine powder & liquid
Contact with concentrated forms of chlorine may result in irritation, chemical burns and even death
  => contact includes clothes, skin, eyes, mouth and inhalation into the lungs
=> Protecting the health and safety of staff is critical
All staff in contact with chlorine must receive basic training in:
  the required personal protective equipment (PPE)
  precautions to be exercised when handling and storing different forms of chlorine, alongside
  basic first-aid measures in the event of accidental contact

## Slide 71
Wear gloves
Wear overalls
Wear a dust mask
Wear safety glasses
GLOVES
OVERALLS
SAFETY GLASSES
DUST MASK
Chlorine powder: Protective personal equipment required for handling
Photo credit: Shutterstock.com

## Slide 72
Chlorine liquid: Protective personal equipment required for handling
Wear gloves
Wear overalls
Wear a face shield
GLOVES
OVERALLS
FACE SHIELD
Any enclosed building used for storage or preparation of chlorine should always be well ventilated.
If chlorine aerosols, mists, vapours or dust are not adequately controlled by ventilation, appropriate respiratory protection should be considered.
Photo credit: Shutterstock.com

## Slide 73
New bag
35 % chlorine
0
months
12
months
Old bag
e.g. 30 % chlorine
For example…
Powder & liquid chlorine may lose strength over time

## Slide 74
Powder & liquid chlorine may lose strength over time
Chlorine liquid solutions are generally less stable than chlorine powder (i.e., lose strength more quickly)
Type of chlorine (approx. % active chlorine concentration) |  | Loss of initial active chlorine concentration (%)1, 2, 3
Chlorine powder | Bleaching powder (35 %) | 5 to 18 % after 40 days
 | High test hypochlorite (70 %) | 
Chlorine liquid | Sodium hypochlorite (15 %) | 50 % after 100 days
 | Sodium hypochlorite (10 %) | 50 % after 220 days
 | Sodium hypochlorite (5 %) | 50 % after 790 days
Source:
1World Health Organisation. Calcium hypochlorite. Fact Sheet 2.19. http://www.who.int/water_sanitation_health/hygiene/emergencies/fs2_19.pdf?ua=1 visited on 13 July, 2015.
2World Health Organisation. Sodium hypochlorite. Fact Sheet 2.20. http://www.who.int/water_sanitation_health/hygiene/emergencies/fs2_20.pdf?ua=1 visited on 13 July, 2015.
3American Water Works Association (2006). Chlorination/chloramination practices and principles. AWWA Manual M20. 2nd Edn. Colorado, United States of America.

## Slide 75
May have important implications for water quality:
  if the chlorine powder or liquid is less concentrated, the risk of chlorine under-dosing may exist (i.e., not adding enough chlorine for effective disinfection)
      may present a microbiological water quality risk
Appropriate chlorine storage practices must be in place to:
  minimize the rate and extent of chorine degradation during storage, and
  protect staff safety
Powder & liquid chlorine may lose strength over time

## Slide 76
Chlorine powder and liquid: Appropriate storage practices
Store in a cool, dry, well ventilated place in air-tight containers
Store away from sunlight
Do not store for excessive periods of time (i.e., many months, years)
Store in chlorine resistant containers
Keep containers closed/sealed when not in use
Check for container leaks/spills regularly
Avoid contact and breathing in chlorine powder dust or chlorine liquid splashes/mists/aerosols
Always mark and date new chlorine stock individually
Use ‘First In First Out’ stock management principles

## Slide 77
Part 2. Practical Chlorination
  Safe handling and storage of chlorine
  Chlorine liquid dosing systems
Contents

## Slide 78
Chlorine liquid dosing systems
Used to dose chlorine liquid into the drinking-water
Two options:
Non-pump-based systems (e.g., gravity)
Pump-based systems

## Slide 79
1. Non-pump based dosing systems
System1 | Basis | Comments
Drip-feed chlorinators | Feeds a constant rate of drops of chlorine liquid solution using a constant head device to maintain the drip feed | Assume constant water flow rate (inaccurate dosing if flow rate changes) Suitable for small supplies Risk of siphoning must be managed
1World Health Organisation. Dosing hypochlorite solutions. Fact Sheet 2.22. http://www.who.int/water_sanitation_health/hygiene/emergencies/fs2_22.pdf?ua=1 visited on 12 August, 2015.
Credit: World Health Organization

## Slide 80
1. Non-pump based dosing systems
System1 | Basis | Comments
Constant head aspirator | Drips a constant rate of chlorine liquid solution using an aspirator and glass tube | Simple, robust device Durable if given appropriate basic maintenance Easy installation Coarse and fine drip-rate control possible Assume constant water flow rate (inaccurate dosing if flow rate changes)
1World Health Organisation. Dosing hypochlorite solutions. Fact Sheet 2.22. http://www.who.int/water_sanitation_health/hygiene/emergencies/fs2_22.pdf?ua=1 visited on 12 August, 2015.
Chlorine tank
Credit: World Health Organization

## Slide 81
1. Non-pump based dosing systems
System1 | Basis | Comments
Gravity feeder | Relies on gravity and a metering orifice/valve to control the flow of chlorine liquid solution | Requires a second tank and ball valve to maintain constant head pressure
1World Health Organisation. Dosing hypochlorite solutions. Fact Sheet 2.22. http://www.who.int/water_sanitation_health/hygiene/emergencies/fs2_22.pdf?ua=1 visited on 12 August, 2015.
Credit: World Health Organization

## Slide 82
1. Non-pump based dosing systems
Lower cost
Simple to operate and maintain (no mechanical parts, servicing)
Not suitable for larger capacity water supply systems
Less accurate and less operational control
=> greater risk of chlorine under-/over-dosing
Suitable for small supplies, limited resource settings

## Slide 83
2. Pump-based dosing systems
Vary in their complexity and design….

## Slide 84
84
Chlorine tank
Dosing pump
Pulsation dampner
Strainer
Chlorine feed line
Filtered water flow
Pressure gauge
Carry water
Injection point
2. Pump-based dosing systems: More basic

## Slide 85
85
2. Pump-based dosing systems: More advanced
Inlet
Bulk Storage Tank
Sloped Floor
Drain
Vent
Transfer Pump
Day
Tank
Dose Pump (Duty/Standby)
Calibration Column
High level alarms
Low level alarms
Pulsation dampner
Pressure relief valve
Load valves
Filtered water flow
Inlet
Bulk storage tank
Sloped floor
Drain
Vent
Transfer pump
Day
tank
Dose Pump (Duty/Standby)
Injection Points
Calibration Column
High level alarms
Low level alarms
Pulsation dampner
Pressure relief valve
Load valves
Filtered water flow
Main process pipe
H
HH
H
HH
LL
L
LL
L
Overflow
Overflow
Feed pipe
LV
LV
Adapted from: Environment Protection Agency (2011). Water treatment manual: Disinfection. Wexford, Ireland.
Credit: Environment Protection Agency, Ireland

## Slide 86
2. Pump-based dosing systems
Allow much greater accuracy and operational control
  may be linked to control signals (e.g. flow-paced, residual trim and associated alarming)
  less risk of chlorine under-/over-dosing
More costly
Require maintenance, servicing and parts
  may require specialised technician and supply chain for parts
Recommended where resources permit

## Slide 87
Part 2. Practical Chlorination
  Safe handling and storage of chlorine
  Chlorine liquid dosing systems
  Chlorine dosing calculations
    How to calculate the chlorine demand
Contents

## Slide 88
Remember….Chlorine demand
Reaction between chlorine and any organic and inorganic material (chlorine reactive substances) present in the water
  During these reactions, chlorine is consumed
  Residual chlorine in the water decreases
Important to understand the chlorine demand of the raw (untreated) water to optimise the chlorine dose

## Slide 89
How to calculate the chlorine demand (Eq. 1)
Chlorine Demand (mg/L) = Actual Chlorine Dose (mg/L) - Total Residual Chlorine (mg/L)
Example:
If the actual chlorine dose is 3 mg/L
The total residual chlorine is 1 mg/L (after 30 minutes contact time), then using Eq. 1:
Chlorine Demand (mg/L) = 3 mg/L - 1 mg/L
= 2 mg/L

## Slide 90
Part 2. Practical Chlorination
  Safe handling and storage of chlorine
  Chlorine liquid dosing systems
  Chlorine dosing calculations
    How to calculate the chlorine demand
    How to calculate the Ct value
Contents

## Slide 91
Remember…. Ct value
Ct is calculated as follows:
Residual chlorine concentration (C) x Contact time (t)
Where:
Residual chlorine: Concentration of residual chlorine (in mg/L)
Contact time: Amount of time (in minutes) there is contact between the chlorine and the water (e.g. detention time in a storage tank, reservoir, or pipe)

## Slide 92
How to calculate the detention time for a storage
Tank volume = 200 m3
Flow = 5 m3/min
Detention time = 200 m3 ÷ 5 m3/min
= 40 min
Detention time (min) = Storage volume (m3) ÷ Flow (m3/min)

## Slide 93
How to calculate the Ct value (Eq. 2)
Ct (min.mg/L) = Residual chlorine concentration (mg/L) x Contact time (min)
Example:
Residual chlorine concentration is 0.5 mg/L
Tank has a detention time of 40 minutes, then using Eq. 2:
Ct (min.mg/L) = 0.5 mg/L x 40 min
= 20 min.mg/L

## Slide 94
Minimum recommended Ct value
However, Ct values should be determined on a site specific basis, considering:
  the temperature of the water
  the pH of the water
  turbidity of the water
  ‘short-circuiting’ within the storage (that is, the potential for preferential flow and reduced mixing/detention time)
A more detailed example for accurately determining the minimum required Ct value using Ct tables is presented in Toolbox C of the accompanying guide
WHO1 recommends a minimum contact time of 30 minutes where the residual chlorine is 0.5 mg/L and the pH is <8
(i.e., 15 min.mg/L)
1 World Health Organization (2011). Guidelines for Drinking-water Quality. 4th Edn. Geneva, Switzerland.

## Slide 95
Part 2. Practical Chlorination
  Safe handling and storage of chlorine
  Chlorine liquid dosing systems
  Chlorine dosing calculations
    How to calculate the chlorine demand
    How to calculate the Ct value
    How to calculate the required chlorine dose
Contents

## Slide 96
How to calculate the required chlorine dose (Eq. 3)
Required Chlorine Dose (mg/L) = Chlorine Demand (mg/L) + Desired Residual Chlorine (mg/L)
Example:
The chlorine demand is known to be 2 mg/L
The desired residual chlorine is 1 mg/L, then using Eq. 3:
Required chlorine dose (mg/L) = 2 mg/L + 1 mg/L
= 3 mg/L

## Slide 97
Part 2. Practical Chlorination
  Safe handling and storage of chlorine
  Chlorine liquid dosing systems
  Chlorine dosing calculations
    How to calculate the chlorine demand
    How to calculate the required chlorine dose
    How to calculate the amount of chlorine powder required to make a chlorine liquid solution
Contents

## Slide 98
Preparing chlorine liquid from chlorine powder
Establish which type of chlorine powder is in use:
  bleaching powder – typically 35 % active chlorine, or
  high test hypochlorite typically 70 % active chlorine
=> if unsure, contact supplier or manufacturer
Consider the age and storage conditions of the chlorine powder
concentration of active chlorine in the chlorine powder may be less than expected if old stock is in use and/or stock has been stored inappropriately

## Slide 99
Preparing chlorine liquid from chlorine powder
Determine what concentration you wish to prepare the chlorine liquid solution:
  typically chlorine liquid solutions are made between 1 and 5 % active chlorine
  higher concentrations of liquid solutions may be prepared in certain circumstances (e.g., pump or bulk storage capacity limitations)
    may result in accumulation of undissolved sediment (or ‘sludge’) from inert material present in the powder (risk of blockages)
    requires appropriate settling time for undissolved sediment and decanting
Appropriate concentration and volume of chlorine liquid solution to be prepared must be determined on a specific basis

## Slide 100
How to calculate the required amount of chlorine powder (Eq. 4)
Weight of chlorine powder (mg/L) =
1 000 x Volume of chlorine liquid required (L) x Desired chlorine liquid concentration (%) Active chlorine concentration in the chlorine powder (%)
Example:
Require 500 L of chlorine liquid solution
Require chlorine liquid concentration to be 2 % active chlorine
Using bleaching powder (35 % active chlorine), then using Eq. 4:
Weight of chlorine powder (mg/L) = 1 000 x 500 L x 2 %
35%
= 28 571 g (or 28.6 kg) per 500 L of water

## Slide 101
Preparing chlorine liquid from chlorine powder
Generally require two containers:
One for mixing and settling of undissolved sediment (e.g., up to 24 hours settling time)
One for decanting settled solution into for storage and dosing
World Health Organisation. Calcium hypochlorite. Fact Sheet 2.19. http://www.who.int/water_sanitation_health/hygiene/emergencies/fs2_19.pdf?ua=1 visited on 13 July, 2015.
Credit: World Health Organization

## Slide 102
Summary of Steps for Preparing Chlorine Liquid from Chlorine Powder
1. Determine what strength chlorine powder you are using
2. Determine the concentration you want the chlorine liquid solution to be
Typically liquid chlorine solutions between 1 to 5 % active chlorine is used
3. Determine how much chlorine powder must be added to prepare the desired chlorine solution
Determine the total volume of liquid chlorine solution required
4. Mix chlorine powder in the desired volume of water in an appropriate container
Bleaching powder ~35 % active chlorine, or
Allow sufficient time for the undissolved powder to settle
High test hypochlorite ~ 70 % active chlorine
May be higher in certain situations
Calculate amount of chlorine powder required for this volume using Equation 4
Pour off (decant) the liquid chlorine solution
Ready to use 

## Slide 103
Part 2. Practical Chlorination
  Safe handling and storage of chlorine
  Chlorine liquid dosing systems
  Chlorine dosing calculations
    How to calculate the chlorine demand
    How to calculate the Ct value
    How to calculate the required chlorine dose
    How to calculate the amount of chlorine powder required to make a chlorine liquid solution
    How to calculate the chlorine dose rate
Contents

## Slide 104
Chlorine dose rate
‘Chlorine dose rate’ means how much chlorine liquid solution you are adding to the water over time
May be measured in various ways
  mL per second
  mL per minute
  L per hour

## Slide 105
How to calculate the chlorine dose rate (Eq. 5)
Chlorine Dose Rate (mL/h) = Required chlorine dose (mg/L) x Treated water flow rate (m3/h) Chlorine liquid concentration (%) ÷ 100
Example:
Require 3 mg/L chlorine dose (see Eq. 3)
Flow rate at the water treatment plant is 100 cubic meters per hour (100 m3/h)
Chlorine liquid concentration is 2 % (see Eq. 4), then using Eq. 5:
Chlorine Dose Rate (mL/h) = 3 mg/L x 100 m3/h
2 % ÷ 100
= 15 000 mL/h (or 250 mL/min)

## Slide 106
How to calculate the actual chlorine dose (Eq. 6)
Actual Chlorine Dose (mg/L) =
[Chlorine dose rate (mL/h) x Chlorine liquid concentration (%)] ÷ 100 Flow rate (m3/h)
Example:
Chlorine dose rate is 6 000 mL/h
Chlorine liquid concentration is 2 % (see Eq. 4)
Flow rate at the water treatment plant is 100 cubic meters per hour (100 m3/h) then using Eq. 6:
Actual Chlorine Dose (mg/L) = (6 000 mL/h x 2 %) ÷ 100
100 m3/h
= 1.2 mg/L
May rearrange Eq. 5 to determine actual chlorine dose; useful for determining chlorine demand (Eq. 1)

## Slide 107
107
4/01/2024
Adjusting the chlorine dose
Always adjust stepwise (i.e., in small increments)
    do not make large adjustments all at once or you risk over-/under-dosing
Always consider time taken for water to turn-over in the tank or pipe before additional adjustments are made
    e.g. may take 2 days for higher chlorinated water to reach a particular monitoring point in the distribution system
    make sure the tank/pipe/section of network is completely replenished with ‘new’ water with the adjusted chlorine dose
Increase the frequency of chlorine monitoring following:
    changes in the chlorine dose
    preparation/delivery of a new batch of chlorine liquid

## Slide 108
108
Chlorine Dosing Cheat Sheet
For a quick and easy way to perform chlorine dosing calculations, see the ‘Chlorine Dosing Cheat Sheet’ described in Toolbox B
  prompts you to input the required information
  automatically performs the calculation
Example:

## Slide 109
Part 2. Practical Chlorination
  Safe handling and storage of chlorine
  Chlorine liquid dosing systems
  Chlorine dosing calculations
    How to calculate the chlorine demand
    How to calculate the Ct value
    How to calculate the required chlorine dose
    How to calculate the amount of chlorine powder required to make a chlorine liquid solution
    How to calculate the chlorine dose rate
  Developing standard operating procedures
Contents

## Slide 110
Standard operating procedures (SOPs)
To be developed for any operational tasks that are performed routinely, including chlorination
Help operational staff perform duties safely, correctly and with consistency
Include important safety information
Examples of information that should be included within SOPs for chlorination….

## Slide 111
Suggested SOPs for chlorination
Calculating the weight of chlorine powder required to make a chlorine liquid batch
Preparing a batch of chlorine liquid from chlorine powder
Calculating the chlorine dose
=> suggested content for each of this is presented on the following slides…

## Slide 112
SOP: Calculating the weight of chlorine powder required to make a chlorine liquid batch
PPE required for safe completion of the task
The type of chlorine powder to be used (e.g., bleaching powder or high test hypochlorite)
The desired solution strength of the chlorine liquid being prepared (e.g., 1 % chlorine liquid solution)
The volume of chlorine liquid solution to be prepared
The calculation used to determine the weight of chlorine powder required
=> For an example see Generic SOP 1 and 2 (Toolbox A)

## Slide 113
SOP: Preparing a batch of chlorine liquid from chlorine powder
PPE required for safe completion of the task
The unit weight of chlorine powder required to prepare a batch of liquid chlorine (e.g., 35 g of bleaching powder per litre of water)
The receptacle that the solution will be mixed in (e.g., dedicated concrete tank or a plastic container)
The means by which the powder will be mixed with the water (e.g., a dedicated mixing device)
The amount of settling time required following mixing and before use
The appropriate chlorine storage conditions
=> For an example see Generic SOP 3 (Toolbox A)

## Slide 114
SOP: Calculating the chlorine dose
PPE required for safe completion of the task
The calculation used to determine the chlorine dose rate based on the strength of the chlorine liquid solution and the water treatment plant flow rate
Precautions to be taken when adjusting the dose rate (including increased monitoring of the chlorine concentration in the drinking-water following adjustment)
=> For an example see Generic SOP 4 (Toolbox A)

## Slide 115
Other chlorination SOPs may include…
Chlorine stock management
Operation and maintenance of chlorine dose pumps
Emergency response procedure in the event of accidental human contact or release to the environment
Emergency response procedure in the event of accidental human contact or release to the environment

## Slide 116
Part 2. Practical Chlorination
  Safe handling and storage of chlorine
  Chlorine liquid dosing systems
  Chlorine dosing calculations
    How to calculate the chlorine demand
    How to calculate the Ct value
    How to calculate the required chlorine dose
    How to calculate the amount of chlorine powder required to make a chlorine liquid solution
    How to calculate the chlorine dose rate
  Developing standard operating procedures
  Chlorine monitoring (operational monitoring)
Contents

## Slide 117
Chorine monitoring (operational monitoring)
Careful monitoring and optimization of the chlorine concentration through the water supply system is critical:
  ensures that sufficient chlorine is added to the water for adequate disinfection and residual protection from recontamination
  minimizing risks of consumer acceptability issues (i.e., taste, odour)
Photo credit: Shutterstock.com

## Slide 118
Chorine monitoring
Should be performed as part of Operational Monitoring
  simple, routine checks to confirm that the measures in place to manage water quality risk are operating effectively (i.e., control measures)
  critical limits determine the point at which the control measures is no longer working within an acceptable range
  corrective actions are then required to restore correction functioning of the control measure and minimise the risk of unsafe water supply

## Slide 119
Operational monitoring is different to verification monitoring
SOIL
AIR
WATERWAYS
SEWAGE
WSP monitoring
Operational monitoring
Asks: Is the control measure effectively working now?
Observations (e.g. visual inspection)
Water sampling and testing
(by the supplier to inform operational decisions)
Verification
Asks: Is the WSP, as a whole, working effectively to deliver safe and acceptable drinking water?
Compliance monitoring
(to confirm compliance with standards; by supplier and surveillance agency)
Audits
consumer surveys
Acknowledgement: Darryl Jackson; Angella Rinehold

## Slide 120
Examples of equipment for chorine monitoring
Chlorine test strips
Chlorine comparator
Chlorine meter
Photo credit: Shutterstock.com
ACCURACY/RESOLOUTION
$$$$$$$$$$$$

## Slide 121
Chorine testing equipment
Test Equipment | Cost | Accuracy/ Resolution | Advantages | Disadvantages
Chlorine test strips | M | L | Easy to use, disposable No calibration/servicing required | Poor degree of resolution (e.g., may only measure in 0.5 mg/L increments) Visual measurement (colour change); open to user interpretation Requires supply chain for replacement strips
Chlorine comparator test kit | M | M | Easy to use Durable for field use No calibration/servicing required | Visual measurement (colour change); open to user interpretation Requires reagents (DPD powder), supply chain
Chlorine meter | H | H | High degree of resolution over a wide range (0.05 to 10 mg/L in 0.01 mg/L increments) Easy to use | Less durable for field use Calibration/servicing required Requires reagents, replacement parts (bulb), supply chain
L - Low; M - Medium; H - High.

## Slide 122
Chorine monitoring
Chlorine monitoring locations in the distribution system should include:
  the start, middle and end of the distribution network
  known water quality trouble spots (that is, where poor water quality has been historically found, such as the end-points of the network, low-flow areas and dead legs)
Number of sample points and the frequency of sampling will differ depending on the specific circumstances of the water supply system
  should be sufficient to manage the risk of sub-optimal chlorination

## Slide 123
Chorine monitoring
Chlorine monitoring should generally occur (for sample point reference, see next slide):
  immediately after chlorine has been added to the water (dosed water; SP1)
  after contact time has elapsed (SP2)
  at the point of entry to the distribution system (SP3)
  throughout the distribution system to the point of consumer delivery (including storage tanks, reservoirs; for example, SP4 to 10; Note - number of sample points will differ depending on the specific circumstances of the water supply system)
  at a frequency that is appropriate to manage the risk of sub-optimal chlorine concentration in the particular drinking-water supply

## Slide 124
Example chorine monitoring locations in a water supply system
WATER TREATMENT PLANT
Source
CHLORINE
CLARIFICATION
FILTRATION
CONTACT
TANK (30 min)
INTERMEDIATE STORAGE TANK
SP9
SP10
SP5
SP6
SP7
SP4
SP8
SP2
SP1
DISTRIBUTION SYSTEM
TREATED WATER STORAGE
SP3

## Slide 125
Chorine monitoring
Feedback of data from chlorine operational monitoring is essential to ensure that the chlorine dose is being optimized
  Chlorine operational monitoring data will indicate if:
    Chlorine dose at the water treatment plant needs to be optimized
    Potential changes in raw/treated water quality
    Potential presence of contamination in storage or distribution
    Likelihood of recontamination during delivery to consumer

## Slide 126
Part 2. Practical Chlorination
  Safe handling and storage of chlorine
  Chlorine liquid dosing systems
  Chlorine dosing calculations
    How to calculate the chlorine demand
    How to calculate the Ct value
    How to calculate the required chlorine dose
    How to calculate the amount of chlorine powder required to make a chlorine liquid solution
    How to calculate the chlorine dose rate
  Developing standard operating procedures
  Chlorine monitoring
General Summary
Contents

## Slide 127
www.egwater.vic.gov.au
4/01/2024
Chlorine is added to water to kill microorganisms
=> kills most microorganisms in a short time
=> not all microorganisms will be killed by chlorine
Chlorine summary…
127

## Slide 128
www.egwater.vic.gov.au
4/01/2024
Chlorine summary…
Chlorine is very reactive
reacts with microorganisms, organic material, sediment, pipe material

## Slide 129
129
www.egwater.vic.gov.au
4/01/2024
Chlorine summary…
Chlorine decay is the decrease in the concentration of chlorine in a water supply system
for this reason, the chlorine concentration decreases in the distribution system

## Slide 130
130
www.egwater.vic.gov.au
4/01/2024
Chlorine summary…
Chlorine demand indicates how much chlorine will be consumed during chlorine reactions
helps inform what chlorine dose is required for effective disinfection
if water has high chlorine demand it consumes more chlorine and needs a high chlorine dose
if water has low chlorine demand it consumes less chlorine and needs a low chlorine dose

## Slide 131
131
www.egwater.vic.gov.au
4/01/2024
Chlorine summary…
Chlorine residual is the concentration of free chlorine remaining after the chlorine demand has been satisfied and disinfection has taken place
critically important water quality parameter for public health
implies that there is residual protection from recontamination from microorganisms during storage/distribution
residual chlorine concentration should always be ≥0.2 mg/L at the point of delivery to the consumer

## Slide 132
132
www.egwater.vic.gov.au
4/01/2024
Chlorine summary…
Chlorine contact time is the amount of time required for effective disinfection to take place
a minimum Ct value of 15 min.mg/L (where pH <8.0) is required in all cases
this is 30 minutes contact time with a residual chlorine concentration of 0.5 mg/L
minimum required Ct value should be determined on a case-by-case basis (see Appendix C of the accompanying manual)

## Slide 133
133
www.egwater.vic.gov.au
4/01/2024
Chlorine summary…
Ct value is influenced by:
pH
temperature
chlorine concentration
turbidity

## Slide 134
134
www.egwater.vic.gov.au
4/01/2024
Chlorine summary…
All forms of chlorine are dangerous to handle
must be handled safely
Powder: Overalls, gloves, safety glasses, dust mask
Liquid: Overalls, gloves and face shield

## Slide 135
135
www.egwater.vic.gov.au
4/01/2024
Chlorine summary…
Chlorine will lose strength over time during storage
chlorine must be stored appropriately
good stock management principles should be applied

## Slide 136
Conditions required for effective disinfection
Chlorine summary…
Turbidity: <1 NTU (lower where possible)
(where < 1 NTU is not possible, <5 NTU should be the aim; above 5 NTU, disinfection should still be practised, but higher chlorine doses or contact times will be required to inactivate harmful microorganisms)
pH: <pH 8.0
(Above pH 8.0, chlorination should still be practised but higher chlorine doses or contact times will be required to inactivate harmful microorganisms)
Minimum contact time: 30 minutes contact time with a minimum residual chlorine concentration of 0.5 mg/L, where the pH of the water is <pH 8.

## Slide 137
Once chlorination at the water treatment plant is complete, the residual chlorine concentration during distribution to the point of delivery should aim to be between 0.2 to 0.5 mg/L.
a minimum residual chlorine concentration of 0.2 mg/L must always be maintained at the point of delivery
The concentration of chlorine in water supplied to consumers should always be <5 mg/L
Chlorine summary…

## Slide 138
Summary…
For sections references, please refer to the accompanying guide

## Slide 139: any
questions...
Photo credit: Shutterstock.com

## Slide 140
Quiz
140
4/01/2024
Multiple choice…..

## Slide 141
Quiz
141
4/01/2024
Q.1) Chlorine is added to water to:
Make it taste better
Kill/inactivate harmful microorganisms
Improve the pH
Remove turbidity

## Slide 142
Quiz
142
4/01/2024
Q.1) Chlorine is added to water to:
Make it taste better
Kill/inactivate harmful microorganisms
Improve the pH
Remove turbidity

## Slide 143
Quiz
143
4/01/2024
Q.2) Microorganisms may be found in:
Soil
Water
Sewage
All of the above

## Slide 144
Quiz
144
4/01/2024
Q.2) Microorganisms may be found in:
Soil
Water
Sewage
All of the above

## Slide 145
Quiz
145
4/01/2024
Q.3) Chlorine will kill/inactivate:
All microorganisms
Some microorganisms
Only bacteria
No microorganisms

## Slide 146
Chlorination Theory and Practice: Assessment
146
4/01/2024
Q.3) Chlorine will kill/inactivate:
All microorganisms
Some microorganisms
Only bacteria
No microorganisms

## Slide 147
Quiz
147
4/01/2024
Q.4) Over time, chlorine powder and liquid will:
Never lose strength
lose strength
Gain strength
Combine to give chlorine gas

## Slide 148
Quiz
148
4/01/2024
Q.4) Over time, chlorine powder and liquid will:
Never lose strength
lose strength
Gain strength
Combine to give chlorine gas

## Slide 149
Quiz
149
4/01/2024
Q.5) Chlorine will react with:
Microorganisms
Other organic material
Inorganic material
All of the above

## Slide 150
Quiz
150
4/01/2024
Q.5) Chlorine will react with:
Microorganisms
Other organic material
Inorganic material
All of the above

## Slide 151
Quiz
151
4/01/2024
Q.6) Due to chlorine decay, the concentration of chlorine during distribution will:
Increase
Decrease
Stay the same
Fluctuate up and down

## Slide 152
Quiz
152
4/01/2024
Q.6) Due to chlorine decay, the concentration of chlorine during distribution will:
Increase
Decrease
Stay the same
Fluctuate up and down

## Slide 153
Quiz
153
4/01/2024
Q.7) If water has high chlorine demand, it will:
Consume more chlorine
Consume very little chlorine
Consume no chlorine
Produce chlorine

## Slide 154
Quiz
154
4/01/2024
Q.7) If water has high chlorine demand, it will:
Consume more chlorine
Consume very little chlorine
Consume no chlorine
Produce chlorine

## Slide 155
Quiz
155
4/01/2024
Q.8) Chlorine residual is the concentration of chlorine:
Before chlorine demand has been satisfied
After chlorine demand has been satisfied
Equal to the total chlorine

## Slide 156
Quiz
156
4/01/2024
Q.8) Chlorine residual is the concentration of chlorine:
Before chlorine demand has been satisfied
After chlorine demand has been satisfied
Equal to the total chlorine

## Slide 157
Quiz
157
4/01/2024
Q.9) Chlorine contact time is the amount of time needed for:
Effective disinfection to occur
For chlorine concentration to decrease to zero
For chlorine to burn your skin
All of the above

## Slide 158
Quiz
158
4/01/2024
Q.9) Chlorine contact time is the amount of time needed for:
Effective disinfection to occur
For chlorine concentration to decrease to zero
For chlorine to burn your skin
All of the above

## Slide 159
Quiz
159
4/01/2024
Q.10) Chlorine contact time depends on the:
pH of the water
Temperature of the water
Chlorine concentration in the water
All of the above

## Slide 160
Quiz
160
4/01/2024
Q.10) Chlorine contact time depends on the:
pH of the water
Temperature of the water
Chlorine concentration in the water
All of the above

## Slide 161
Quiz
161
4/01/2024
Q.11) Chlorine disinfection works best when turbidity is:
>1 NTU
<1 NTU
>5 NTU
Turbidity does not impact disinfection

## Slide 162
Quiz
162
4/01/2024
Q.11) Chlorine disinfection works best when turbidity is:
>1 NTU
<1 NTU
>5 NTU
Turbidity does not impact disinfection

## Slide 163
Quiz
163
4/01/2024
Q.12) The residual chlorine concentration in the distribution network should always be:
Undetectable
<0.2 mg/L
≥0.2 mg/L
>5 mg/L

## Slide 164
Quiz
164
4/01/2024
Q.12) The residual chlorine concentration in the distribution network should always be:
Undetectable
<0.2 mg/L
≥0.2 mg/L
>5 mg/L

## Slide 165
Quiz
165
4/01/2024
Q.13) If the residual chlorine concentration is <0.2 mg/L in distribution samples, the water is:
Safe from recontamination by microorganisms
At risk from recontamination by microorganisms
Unpleasant taste and odor
None of the above

## Slide 166
Quiz
166
4/01/2024
Q.13) If the residual chlorine dose is <0.2 mg/L in the distribution network, the water is:
Safe from recontamination by microorganisms
At risk from recontamination by microorganisms
Unpleasant taste and odor
None of the above

## Slide 167
167
4/01/2024
Q.14) The chlorine dose at the water treatment plant should always be:
1 mg/L
<0.2 mg/L
5 mg/L
Sufficient to ensure effective disinfection and a chlorine concentration ≥0.2 mg/L to the point of consumer delivery
Quiz

## Slide 168
168
4/01/2024
Q.14) The chlorine dose at the water treatment plant should always be:
1 mg/L
<0.2 mg/L
5 mg/L
Sufficient to ensure effective disinfection and a chlorine concentration ≥0.2 mg/L to the point of consumer delivery
Quiz

## Slide 169
169
4/01/2024
Q.15) For effective chlorination, the pH of the water should always be:
>pH 8.5
<pH 8.5
pH does not impact chlorination
Quiz

## Slide 170
170
4/01/2024
Q.15) For effective chlorination, the pH of the water should always be:
>pH 8.5
<pH 8.5
pH does not impact chlorination
Quiz