## Slide 1
Water safety plan
Step-by-step risk management for drinking-water suppliers
Training package
Notes: 1
Cover slide

## Slide 2
NOTE to trainer(s)
Delete this slide prior to delivering the presentation
This presentation and the associated training materials have been developed by the World Health Organization and International Water Association (2025) for adaptation and use by those conducting water safety planning training workshops.
Under the terms of this licence, you may copy, redistribute and adapt the work for non-commercial purposes, provided the work is appropriately cited, as indicated below. In any use of this work, there should be no suggestion that WHO endorses any specific organization, products or services. The use of the WHO logo is not permitted. If you adapt the work, then you must license your work under the same or equivalent Creative Commons licence
All reasonable precautions have been taken to verify the information contained in these materials. However, the material is being distributed without warranty of any kind, either expressed or implied. The responsibility for the interpretation and use of the material lies with the reader. In no event shall the World Health Organization or International Water Association be liable for damages arising from its use.
© World Health Organization 2025. Some rights reserved. This work is available under the CC BY-NC-SA 3.0 IGO licence.
Suggested citation. Water safety plan: step-by-step risk management for drinking-water suppliers. Training package: powerpoint slides. Geneva: World Health Organization; 2025 (WHO/HEP/ECH/WSH/2025.58).

## Slide 3
NOTE to trainer(s)
These training materials are based on Water safety plan manual, 2nd edition (WHO & IWA, 2023).
These materials have been developed for a 4-day training event incorporating a partial-day field visit, but they can be adapted to accommodate other training durations and approaches, as preferred.
Customization of these training materials to reflect the local context will contribute greatly to positive outcomes and is highly recommended.
Delete this slide prior to delivering the presentation

## Slide 4
Trainer name(s)
Affiliation
Insert
trainer
photo
TRAINER introductions

## Slide 5
Appreciate the value of water safety planning
Understand water safety plan (WSP) principles and steps
Understand how WSPs provide a framework to strengthen equitable access to safe drinking-water supplies that are more resilient to climate change
Have sufficient knowledge and confidence to begin to develop and implement WSPs
This workshop is an introduction to WSP principles and practices
WORKSHOP objectives
By the end of this workshop, all participants should 

## Slide 6
PRACTICAL
WORKSHOP approach
This workshop will be 
PARTICIPATORY
INTENSIVE
Practice the theory introduced in both classroom and field
Often a 5+ day training!
Engage with activities, share ideas, ask questions

## Slide 7
WORKSHOP overview
WSP introduction, modules 2-3
DAY 1
DAY 2
Modules 4-7, field trip briefing
DAY 3
Field trip
DAY 4
Field trip sharing, modules 8-10 and module 1, wrap-up, next steps

## Slide 8
RESOURCE review
Resources at your tables 
Workshop
program
Participant
Workbook

## Slide 9
PARTICIPANT introductions
Who’s who in the room?
Tell us about yourself in max. 10 seconds
What is your name?
What is your organization and job title?
What is your WSP experience?
Answer either: new to WSPs, some experience, or a lot of experience
What is one fun fact about yourself?
e.g. hobby, favourite movie, favourite food, phobia, languages you speak…

## Slide 10
WSP introduction
WSP background
What is a WSP?
Why do we need WSPs?
WSP drivers
Benefits of WSPs
Global WSP uptake

## Slide 11
WSPs introduced by WHO in Guidelines for drinking-water quality (3rd Edition, 2004)
“The most effective means of consistently ensuring the safety of a drinking water supply.”
WSP background

## Slide 12
A proactive risk assessment and risk management approach to help ensure drinking-water safety, encompassing the entire drinking-water supply, from catchment to consumer
WATER SAFETY PLAN 
WHAT is a WSP?
Notes: 12

## Slide 13
Water safety planning asks three questions
01
03
How can we better manage the risks?
What are the priority risks?
How can we confirm the ongoing effectiveness of the WSP?
Notes: 13

## Slide 14
Credit: Ollivier Girard/CIFOR via flickr.com (CC BY-NC-ND 2.0)
WSPs involve…
Preventing contamination at the source
Removing/ reducing contamination by water treatment
Preventing recontamination in storage and distribution
Preventing recontamination at the household
Picture 1: Ollivier Girard/CIFOR via flickr.com (CC BY-NC-ND 2.0)
Pictures 2-4: WHO/Rory Moses McKeown

## Slide 15
Understanding the complete water supply system
Focusing initially on priority risks
Monitoring to make sure all parts of the system continue to work properly
Putting barriers and management systems in place to proactively manage these risks
Involving all stakeholders
Identifying where and how the problems could arise
WHAT is a WSP?
A proactive management system to ensure safe drinking-water by 
5
After Water safety planning for urban water supply systems an introduction (WHO, 2024)

## Slide 16
WSPs use a “multi-barrier approach”
Multiple-barriers in action to prevent microbial contamination 
Example: Restrictions on land use in catchment
Example: Sand filtration & disinfection at a water treatment plant
Example: Maintaining residual disinfection during distribution
Example:
Household treatment and safe storage practices
1
After Water safety planning for urban water supply systems an introduction (WHO, 2024)
Notes: Central to water safety planning is the “multiple-barrier” approach.
As illustrated in this diagram, this is across the entire system from catchment …..to …….the user (or consumer).
Here we see if one barrier fails, e.g. source protection measures [CLICK], there are other barriers in place downstream to minimize the risk of microbial contamination e.g. filtration, disinfection and household treatment.

## Slide 17
Without a risk management approach, water suppliers must rely only on END-PRODUCT TESTING to confirm water safety
WHY do we need WSPs?
Notes: 17

## Slide 18
Water microbially contaminated
Water sampled & tested
Test results
* E. coli *
Day 0
Boil water advisory issued to consumers
TIME
WHY do we need WSPs?
4
Day 7
Day 9
Day 10
End-product testing scenario
Contaminated water consumed
Notes: 18

## Slide 19
Working in groups, make a list of the problems with relying on end-product testing to ensure water safety.
EXERCISE:
Limitations of end-product testing
10 minutes
(5 to complete; 5 to discuss)
After exercise, review examples on following slide…

## Slide 20
Limitations of end-product testing include 
  Reactive approach (problem has already occurred)
  Test results provide a “spot check” only (problems can be missed in space and time)
  Limited laboratory/equipment capacity
  Testing can be very expensive
  May not be clear what went wrong, where and when (supplier may not know how to correct problem)
WHY do we need WSPs?
TOO LITTLE, TOO LATE!
1
Notes: 20
Too little – does not give you the information needed to identify the source of the problem, pr prevent it from happening again.
Too late – unsafe water has already been delivered.

## Slide 21
WHY do we need WSPs?
Water quality testing is an important component of water supply system management…
…but it is not enough to ensure water safety.
Need a proactive approach to ensure water safety through good management of the complete water supply system  WSP
Notes: 21

## Slide 22
WSPs play a key role in delivering safe drinking-water
Framework for safe drinking-water 
WSPs are one of three functions recommended by WHO to ensure drinking-water safety
can help water suppliers to achieve drinking-water quality targets
After Guidelines for drinking-water quality (WHO, 2022)
Drinking-water quality targets
established based on health considerations
Water supply managed by a
Water safety plan
Verified by
Independent surveillance

## Slide 23
Increased focus on proactive management to ensure safe delivery of drinking-water services
WSPs and the Sustainable Development Goals (SDGs)
Notes: WSPs are a tool to help achieve the SDGs
SDG is central to achieving the SDG agenda as a whole.
Beyond 2030, WSPs will continue to play a central role as part of the future development agenda.

## Slide 24
Regional or national drivers, such as drinking-water quality policies and legal instruments, for example:
National standards requiring WSPs in Lao People’s Democratic Republic
European Union Drinking Water Directive
Sri Lanka national policy on drinking-water safety
WSP policies or regulations have been formally approved in over 60 countries*
*WHO global tracking database (as at 2022)
WSP drivers
Notes: 24

## Slide 25
Improved system understanding
Improved stakeholder collaboration
Prioritized improvement needs
Improved operations and management
Cost savings via improved operational efficiencies
Reductions in non-revenue water
Improved infrastructure
Leveraged financial support
WSP OUTCOMES
WSP IMPACTS
Leading to
Improved water quality
Improved service delivery
Improved health
BENEFITS of WSPs
Suppliers Consumers Health authorities
Notes: 25

## Slide 26
Garbage
In
Garbage
Out
We get out of WSPs what we put into them.
Attitude is key!
=
MANY WSP benefits, however GIGO principle applies…
Notes: 26

## Slide 27
WSPs provide resilience to future shocks and uncertainty
WSPs support future planning for foreseen and unforeseen events
WSPs can strengthen the resilience of the water supply e.g.
Support business continuity planning
Strengthen emergency preparedness and response planning
Help ensure robust supply chains (e.g. treatment additives, consumable reagents for testing)
Notes: 27
Future and unforeseen events can include natural disasters, conflict, epidemics/pandemics, migration, urbanization

## Slide 28
WSPs and building climate resilience
WSPs can help to prioritize and manage current and future climate threats
Considers the implications of climate change at each stage of the water supply
Example climate impacts | Hazardous event | Example improvement measures needed
Increased temperature Reduced precipitation Increased drought | Reduced water quantity due to reduced rainfall and increased demand | Catchment/source Provision of additional boreholes to supplement existing water source
 |  | Treatment Backwash water recovery program to minimize water wastage
 |  | Distribution/storage Leak detection Mains repair/replacement programme
 |  | Household User education on water conservation during drought periods

## Slide 29
WSPs and enhancing equitable access to safe drinking-water
Vulnerable and disadvantaged groups can be explicitly considered in WSPs to help reduce inequalities e.g.
Considering users in informal settlements when assessing risks
Including all users in monitoring programmes
Developing emergency response plans that consider the needs of different groups
Notes: This figure illustrates the diversity of user groups that may be encountered in a water supply system.

## Slide 30
GLOBAL WSP uptake
How many countries have implemented WSPs?
?
Notes: 30

## Slide 31
*
* Or equivalent risk assessment and risk management approaches.
WHO/IWA (2017) Global status report on water safety plans. Geneva, Switzerland.
GLOBAL WSP uptake
>90
countries have implemented WSPs*
Notes: 31

## Slide 32
Example on next slide…
Working in groups, and as a team, read the instructions in the Participant Workbook (page 3).
Choosing from the list provided, complete the table by matching each water-related hazard with the signs and source of the hazard. Review answers together.
Activity 1 – Workbook page 3
ACTIVITY 1:
Water quality and health
15 minutes
(10 to complete; 5 to review)

## Slide 33
Potential signs | Possible hazard | Possible contamination source (or hazardous event)
Acute health issues |  | 
Diarrhoea and dysentery (including occasional outbreaks of cholera and typhoid fever) and other waterborne infections such as hepatitis are widespread within the community, particularly affecting the young, old and health compromised |  | Open defecation or nearby sanitation facilities; agriculture (use of manure) or wildlife; dirty water with suspended particles such as silt, clay or organic matter (often from flood waters or following rainstorms)
After exercise, review answers on following slides…
1
EXERCISE:
Water quality and health
EXAMPLE:
Microbial pathogens

## Slide 34
Potential signs | Possible hazard | Possible contamination source (or hazardous event)
Acute health issues |  | 
Diarrhoea and dysentery (including occasional outbreaks of cholera and typhoid fever) and other waterborne infections such as hepatitis are widespread within the community, particularly affecting the young, old and health compromised | Microbial pathogens | Open defecation or nearby sanitation facilities; agriculture (use of manure) or wildlife; dirty water with suspended particles such as silt, clay or organic matter (often from flood waters or following rainstorms)
Methaemoglobinaemia in bottle-fed infants (or "blue baby syndrome") | High levels of nitrates/nitrites | Sewage discharges; poorly maintained septic tank; animal manure and runoff from agriculture
1

## Slide 35
Potential signs | Possible hazard | Possible contamination source (or hazardous event)
Chronic health issues |  | 
Mottling and staining of teeth in young children and teenagers; brittle bones and crippling | High fluoride levels | Naturally occurring in some groundwaters
Pigmentation changes (melanosis) and thickening of the skin (hyperkeratosis), increased rates of cancers | High arsenic levels | Naturally occurring in some groundwaters
Skin irritation (skin rash, hives, itchy eyes and throat); tingling around the mouth and fingertips; slurred speech; animals who drink the water may die | Algae and algal toxins | High nutrient levels in warm and stagnant surface water (ponds, tanks)
3

## Slide 36
Potential signs | Possible hazard | Possible contamination source (or hazardous event)
Acceptability issues |  | 
Stains on fixtures or laundry; coloured water with metallic taste | High metal concentrations | Naturally occurring in some groundwaters; may result from corroding pipes in the distribution system or from "overturning" of reservoirs
Unpleasantly salty taste (may pose health concern to those on sodium-restricted diets) | High sodium chloride levels | Naturally occurring in some groundwaters; may be from seawater (coastal areas) or caused by evaporation residue in irrigated areas (hot climates)
Rotten egg odour and taste; corrosive black spots in pipes | High sulfide levels | Naturally occurring in some groundwaters; could indicate industrial waste, oil, coal or stagnant water
3

## Slide 37
Potential signs | Possible hazard | Possible contamination source (or hazardous event)
Acceptability issues |  | 
Brown-coloured water without particles (not direct harmful to health but could result in high levels of disinfection by-products if water is chlorinated) | High levels of natural organic matter | Naturally occurring in some surface waters from lakes or rivers with submerged vegetation
Soap does not lather; white scale builds up on pots or kettles when water is heated (not harmful to health, but may make water difficult to treat and use) | High hardness (calcium and magnesium) | Usually from limestone or chalk aquifers
2

## Slide 38
WHO/IWA (2023)
Reflects over 15 years of practical experience since the first edition (2009)
BASIS of this WSP training
Streamlined integration of enhancing climate resilience and equity in WSPs
Notes: 38

## Slide 39
Mod 2: Describing the system
Mod 5: Planning for improvement
Mod 6: Monitoring control measures
Mod 7: Verifying the effectiveness of water safety planning
Mod 8: Strengthening management procedures
Mod 9: Strengthening WSP supporting programmes
Mod 3: Identifying hazards and hazardous events
Mod 4: Validating existing control measures and assessing risks
Mod 10: Reviewing and updating the WSP
Mod 1: Assembling the WSP team
DAY 1
DAY 2
DAY 4
10 WSP modules

## Slide 40
MODULE
I
Assembling the WSP team
Notes: 40
Module slide 1

## Slide 41
Outlines roles and responsibilities for the team, and stakeholder engagement.
Participants first need to understand the full WSP process.
Only then can you fully appreciate who needs to be involved, when, and why, to ensure the overall undertaking is effective.
MODULE 1
Will discuss on Day 4
Notes: 41

## Slide 42
MODULE
2
Describing the system
How does the system deliver drinking-water from catchment to consumer?
Notes: 42
Module slide 1

## Slide 43
MODULE 2 overview
1
2
3
WHAT WE DO:
Develop an accurate, up-to-date description of the complete water supply system
WHY WE DO IT:
To contribute to system understanding and to facilitate identification of system vulnerabilities in subsequent steps
HOW WE DO IT:
Gather, document and update system information (in words and supporting diagrams)
Confirm the accuracy of the system description

## Slide 44
What should we describe at each step?
?
Catchment/ source
Treatment
Storage & distribution
User
Describe the complete water supply system
List water quality targets / standards
Include known / suspected problems or vulnerabilities
KEY ACTION 1:
Gather, document and update system information

## Slide 45
Water source(s), yields, catchment land use, source water quality/issues, abstraction details, climate information/ projections, etc.
Treatment processes, chemicals used, treatment capacity (versus production), treated water quality/issues, etc.
Storage tanks
(number, capacity, age, material), pipeline information (age, material), tapstands, delivery tankers, kiosks, etc.
Consumer practices (collection, storage, treatment, handling), including vulnerable and disadvantaged groups, etc.
3
Catchment/ source
Treatment
Storage & distribution
User
INCLUDE summarized information to help identify vulnerabilities

## Slide 46
Intended use | Intended users
The water supplied is intended for consumption, food preparation, bathing and laundry. | GENERAL POPULATION. The intended users do not include those that are significantly immuno-compromised or industries with special water quality needs. These groups are advised to provide additional point-of-use treatment.
What is meant by “general population”?
Do we need to be more specific to ensure equitable benefit?
1
INCLUDE information on the “use” and “users” of the water
EXAMPLE:

## Slide 47
If the diverse water experiences of different user groups are not considered through the WSP process, the WSP may overlook important risks affecting some users
Household tap (most residents)
Public tap
(informal settlements)
Remember to consider all users, including vulnerable & disadvantaged groups
EXAMPLE
Credit: WHO/RM McKeown
1
WHY it is important to consider all users

## Slide 48
1
A great deal of information can be presented on a diagram
80 m
20 L/s
Well #1
Well #2
Ground-level raw water storage
Elevated treated water storage tank
Pumps
UV
75 m
15 L/s
Concrete Uncovered
Built 1980
Steel Covered
Built 2000
5 000 customers, Household connections
Duty/standby
Distribution system
500 KL
600 KL
DEVELOP a system diagram
Raw Water
Treated Water
Raw Water
Treated Water
Notes: Discuss this diagram in detail, including:
Why is it valuable to record upstream activities or conditions on the diagram? (Example answer: to understand threats to source water quality.)
Why is it valuable to show the number of pumps and specify duty or standby? (Example answer: to facilitate hazard identification and risk assessment by prompting consideration of what might happen in the event of a pump failure.)
Why is it valuable to record system details (tank size/material, year constructed, etc.) on the diagrams? (Example answer: it is a clear and simple way to record and display system details important for water quality; important for hazard identification; lends itself to easy review and update.)

## Slide 49
Raw Water
Treated Water
Consider climate and equity information
80 m
20 L/s
Well #1
Well #2
Ground-level raw water storage
Elevated treated water storage tank
Pumps
UV
75 m
15 L/s
Concrete Uncovered
Built 1980
Steel Covered
Built 2000
5 000 customers, Household connections
Use surface water during flood-related supply outages
Duty/standby
Distribution system
500 KL
600 KL
DEVELOP a system diagram
Annual rainfall:
2035 – 1750 mm
Projected to be subject to flooding by 2035
60 m
20 L/s
Well #3
Future water source
(high fluoride)
700 users in informal settlements rely on tapstands
Often low chlorine residual

## Slide 50
System diagrams help to:
strengthen conceptual understanding of the complete system
clarify water flow, linkages, responsibilities and vulnerabilities
Create system diagrams with sufficient detail to help identify problems or potential problems
If needed, consider creating diagrams at two levels:
SYSTEM DIAGRAMS are an important part of the system description
Level 1: system overview (catchment to consumer)
Level 2: water treatment plant details
!

## Slide 51
Treated Water
Raw Water
Treated Water
LEVEL 1:
System overview
Duty/ standby pump
Cattle farm
Village
Raw water storage reservoir for irrigation, 1990
1 ML
Treated water storage, steel, 1990
Duty/ standby pump
Blue River WTP
High-level area,
20 000 customers, Household connections
Low-level area, 10 000 customers, 50% household connections, 50% public tap stands
See detailed drawing of WTP
500 KL
Blue River
5 ML/d

## Slide 52
Blue River Water Treatment Plant (WTP)
(5 ML/day, built 2014)
Rapid mix
Flocculation
Clarification
Filtration
Raw water storage reservoir
5 ML
Clear water storage tank
1 ML
Duty/ standby pumps
Chlorine
Alum
LEVEL 2:
Water treatment plant details
Raw Water
Treated Water
Notes: Flag that additional details such as control points (e.g. turbidity meters at individual filters), sample points, and the number of unit processes (e.g. rapid sand filters x 6) would also be advantageous.

## Slide 53
Walk the system!
Don’t rely on a desktop review only
Follow the flow of water and field verify that the description is thorough and accurate.
KEY ACTION 2:
Confirm the accuracy of the system description
  Interview relevant field staff, operators or stakeholders to confirm accuracy of information
  Ensure that the system description is consistent with accurate data and reports
  Update the system description based on the outcomes of these activities

## Slide 54
Consider this water supply scenario:
EXERCISE:
Where does the WSP end?
10 minutes
(5 in groups; 5 in plenary)
Intermittent supply is standard operation
Consumers generally receiving water once every one or two weeks
Household rooftop tanks are part of the supply chain
Credit: WHO/RM McKeown
Notes: Ask participants to consider:
The fact that intermittent supply is standard operation, with consumers generally receiving water once every one or two weeks
Rooftop tanks are part of the supply chain.

## Slide 55
Working in groups, consider where the WSP should end:
10 minutes
(5 in groups; 5 in plenary)
At the water meter? (before rooftop storage)
At the tap? (after rooftop storage)
At the point of consumption? (after household treatment)
EXERCISE:
Where does the WSP end?
Notes: Get participants to self organize into three areas of the room according to their answer i.e. one corner for “water meter”; opposite corner for “point of consumption”; middle of the room for “tap”.
Get each group to discuss their reasons and to nominate a spokesperson to defend the groups decision.

## Slide 56
Part I: Working in groups, create system diagrams as described in the Participant Workbook (page 5).
Part II: Review diagrams in table group pairs assigned by the trainer.
ACTIVITY 2:
System diagram
50 minutes
(40 to complete; 10 to review)
Activity 2 – Workbook page 5

## Slide 57
ACTIVITY 2:
System diagram – hints & tips
Reminder: system diagrams should include sufficient detail to help identify problems or potential problems
Level 1: system overview (catchment to consumer)
Level 2: water treatment plant details

## Slide 58
MODULE
3
Identifying hazards and hazardous events
What could go wrong?
Notes: 58
Module slide 1

## Slide 59
HOW WE DO IT:
For each step in the water supply chain, identify hazards and hazardous events that could contaminate or compromise the water supply
MODULE 3 overview
1
2
3
WHAT WE DO:
List the issues that may threaten the safety and adequacy of the water supply
WHY WE DO IT:
To understand what could go wrong in the entire system to ensure important risks can be identified and managed

## Slide 60
DEFINITIONS
HAZARD
A contaminant or condition that may adversely affect the supply of safe drinking-water
HAZARDOUS EVENT
An event that results in a hazard being introduced to, or inadequately removed from, the water supply

## Slide 61
HAZARD
Large boulder
HAZARDOUS EVENT
The houses are damaged because of heavy rains that destabilize the hillside, releasing the boulder
2
HAZARD vs. hazardous event

## Slide 62
HAZARD types
Microbial
e.g. pathogens such as E. coli, Legionella, Cryptosporidium, norovirus, enterovirus
Chemical
e.g. arsenic, fluoride, lead, manganese, nitrate, iron, synthetic chemicals, pesticides
Radiological
e.g. radionuclides, radium, uranium, tritium
Acceptability
e.g. taste/odour, colour, turbidity, hardness
Quantity-related
e.g. insufficient water for hydration, hygiene, domestic needs
Generally classify hazard types as 

## Slide 63
HAZARDOUS EVENT  Source water is faecally contaminated because of faecal run-off into the source water from cattle grazing
HAZARD TYPE  Microbial
HAZARDOUS EVENT  Source water is chemically contaminated because of pesticide run-off into source water
HAZARD TYPE Chemical
2
HAZARDS and hazardous events
Notes: Ask participants the answer, one row at a time, before clicking the animation.

## Slide 64
Catchment/ source | Animal waste in runoff; industrial discharges; onsite-sanitation overflow during flood; agricultural chemicals in runoff; natural chemicals in groundwater; sediment from bushfires
Treatment | Inadequate coagulation; filter clogging/ breakthrough; inadequate disinfection (underdose or insufficient contact time); chemical overdose; power failure; pump failure
Storage & distribution | Birds/animals entering the storage; flooding of pump stations; leaky pipes; poor pipeline repair practices; backflow
Consumer practices | Transport from tapstand in open/unsafe vessels; unsafe storage practices; poor hygiene practices; improper household treatment practices
3
EXAMPLES of possible problems
What are possible problems at each step?
?

## Slide 65
When describing hazardous events, BE SPECIFIC!
Clearly indicate what hazard could be introduced, and how.
TIP A good hazardous event reads like this:
X happens (to the water supply) because of Y
DESCRIBING hazardous events

## Slide 66
Source water becomes faecally contaminated (X) because of discharge of untreated domestic waste from households (Y)
Water in the pipe network becomes contaminated (X) because of unsanitary pipeline repair practices (Y)
Water is over- or under-dosed with chlorine (X) because of insufficient operator training (Y)
Y = How it can happen (i.e. cause)
DESCRIBING hazardous events
X happens (to the water supply) because of Y
EXAMPLES:
X = What can happen to the water supply

## Slide 67
WEAK EXAMPLE
STRONGER EXAMPLES
Hazardous event: The source water is chemically contaminated (X) due to use of pesticides on crops and runoff during rains (Y)
X = What can happen to the water supply
Y = How it can happen (i.e. cause)
Are these clear enough?
2
DESCRIBING hazardous events
Hazardous event: The source water is faecally contaminated (X) due to use of animal waste on crops and runoff during heavy rains (Y)
Hazardous event: Agriculture in the catchment
Notes: Make clear the point that if you do not define clearly in module 3 – this affects the risk assessment in Module 4, and subsequent modules.

## Slide 68
Hazardous event: Old pipes
Hazardous event: Acceptability and microbial contaminants enter the pipe network (X) due to leaks in old pipes (Y)
Hazardous event: The water supply is chemically contaminated (X) due to leaching of lead from old pipes (Y)
X = What can happen to the water supply
Y = How it can happen (i.e. cause)
Not clear enough
1
DESCRIBING hazardous events
WEAK EXAMPLE
STRONGER EXAMPLES

## Slide 69
When identifying hazardous events, consider each step in the water supply chain and ask:
  What could potentially go wrong at this location?
  What is wrong now, what has gone wrong in the past, and what could possibly go wrong in the future?
  Consider climate information & projections!
Identifying hazardous events should involve:
  Field visits/site inspections (incl. discussions with field staff, stakeholders)
  Desktop review of Module 2 system diagrams (detailed and accurate!)
  Consideration of all user groups
IDENTIFYING hazardous events

## Slide 70
Working all together in plenary, make a bullet list of some potential problems in the pictures on the next slide.
Then, translate these into clearly-defined hazardous events/hazard types.
15 minutes
EXERCISE:
Hazard brainstorm
Hazardous event The source water is faecally contaminated (X) due to the animals defecating in the river at the abstraction point (Y)
Hazard Microbial (M)
EXAMPLE
Picture 1: Ollivier Girard/CIFOR via flickr.com (CC BY-NC-ND 2.0)

## Slide 71
EXERCISE:
Dug well hazard brainstorm
6
Photo credit: Photos 1, 5, 6 - WHO/RMK
Photos 2, 3 and 4 - WHO/Oliver Schmoll
Hazardous event: Water losses because of pipe leaks
Hazard: Quantity
Hazardous event: Contamination of stored water because of missing tank cover
Hazard: Microbial
Hazardous event: Chemical contamination of water because of use of a chemical container to store household water
Hazard: Chemical Acceptability
Hazardous event: Ingress of contaminated surface runoff because of broken spring box
Hazard: Microbial
Hazardous event: Microbial contamination from insects or rodents accessing the reservoir because of damaged screens
Hazard: Microbial
Hazardous event: Household well water microbiologically contaminated during collection because of flooding
Hazard: Microbial
After Strengthening drinking-water surveillance using risk-based approaches – training package (WHO EURO, 2025)

## Slide 72
Working in groups, carry out Activity 3 in the Participant Workbook (page 7).
50 minutes
(40 to complete; 10 to review)
ACTIVITY 3:
Hazard identification
Workbook Activity 3 (page 7)

## Slide 73
Consider these real-world examples that highlight the importance of detailed and accurate system diagrams…..
CASE EXAMPLES:
Identifying hazards/hazardous events

## Slide 74
AUSTRALIA: Hazard detected by field verifying system diagram
1
WHAT is the problem?
Raw Water
Treated Water
Rapid mix
Flocculation
Clarification
Filtration
Raw water storage reservoir
5 ML
Clear water storage tank
1 ML
Duty/ standby pumps
Cl2
Alum
Cl2
!
Notes: This story provides a good of example of why it is important to field verify the system diagrams. For this system in Australia, the operators believed that the chlorine was added at the INLET of the clearwater storage tank. However, during the process of field verifying the system diagram, they discovered that the chlorine was actually added at the tank outlet due to a plumbing error. Ask participants what is the associated hazard.
The hazard here is that chlorine requires “contact time” with the water to kill microorganisms, and that “contact time” should be provided in the clearwater storage tank.
When the chlorine is injected into the line AFTER clearwater storage (rather than before), the water may reach the first consumers before chlorine has had time to kill the microbes. After making this discovery, the operators changed the chlorine addition point from the tank outlet to the tank inlet.
This story provides a good of example of why it is important to develop detailed and accurate system drawings. (Without the detailed diagram, this supplier would not have identified and resolved this important system hazard.)

## Slide 75
LIBERIA: Hazard detected by field inspection
1
WHAT is the problem?
Boreholes
Chlorine
Treated water
Elevated
storage
Main supply
pipeline
Users
Credit: WHO/RM McKeown
Notes: During a field visit as part of Module 3, the main supply pipeline – that is, the water transmission line between the treated water storage tank and the distribution system – was found to be exposed because surface water following heavy rainfall had washed away the ground cover. The pipe was beside a main road that was subject to heavy vehicular traffic.
If the pipe had been damaged, the water supply to the town would have to be shut off for an extended period to allow repair work. This would lead to a prolonged supply outage, as well as microbial and acceptability risks associated with depressurizing the water main and repairing the pipeline.

## Slide 76
MORAL OF THE STORIES:
Detailed and accurate system diagrams (Module 2) play an important role in hazard identification (Module 3)
Desk-top identification of hazards/hazardous events alone is insufficient to detect all threats within a system → field visits are required!
SYSTEM DIAGRAMS support hazard identification

## Slide 77
10 WSP modules
Mod 2: Describing the system
Mod 5: Planning for improvement
Mod 6: Monitoring control measures
Mod 7: Verifying the effectiveness of water safety planning
Mod 8: Strengthening management procedures
Mod 9: Strengthening WSP supporting programmes
Mod 3: Identifying hazards and hazardous events
Mod 4: Validating existing control measures and assessing risks
Mod 10: Reviewing and updating the WSP
Mod 1: Assembling the WSP team
DAY 1
DAY 2
DAY 4
Notes:   Flag that Day 1 is complete
  Note to facilitator – if there is still time left on day 1; Module 4 could be started (e.g. Module 4 key actions 1 and possibly 2), and the programme adjusted accordingly.

## Slide 78
DISCUSSION and questions?
Notes: 78

## Slide 79
That’s all for today!
Credit: WHO/RM McKeown